## 1
Health Index Asset Category | Asset Register Category
LV OHL Support | LV Poles
LV UGB | LV UGB
LV Switchgear and Other | LV Board (WM)
LV Switchgear and Other | LV Board (X-type Network) (WM)
LV Switchgear and Other | LV Circuit Breaker
LV Switchgear and Other | LV Pillar (ID)
LV Switchgear and Other | LV Pillar (OD at Substation)
LV Switchgear and Other | LV Pillar (OD not at a Substation)
HV OHL Support - Poles | 6.6/11kV Poles
HV OHL Support - Poles | 20kV Poles
HV Switchgear (GM) - Primary | 6.6/11kV CB (GM) Primary
HV Switchgear (GM) - Primary | 20kV CB (GM) Primary
HV Switchgear (GM) - Distribution | 6.6/11kV CB (GM) Secondary
HV Switchgear (GM) - Distribution | 6.6/11kV RMU
HV Switchgear (GM) - Distribution | 6.6/11kV X-type RMU
HV Switchgear (GM) - Distribution | 6.6/11kV Switch (GM)
HV Switchgear (GM) - Distribution | 20kV CB (GM) Secondary
HV Switchgear (GM) - Distribution | 20kV RMU
HV Switchgear (GM) - Distribution | 20kV Switch (GM)
HV Transformer (GM) | 6.6/11kV Transformer (GM)
HV Transformer (GM) | 20kV Transformer (GM)
EHV OHL Support - Poles | 33kV Pole
EHV OHL Support - Poles | 66kV Pole
EHV OHL Fittings | 33kV Fittings
EHV OHL Fittings | 66kV Fittings
EHV OHL Conductor (Tower Lines) | 33kV OHL (Tower Line) Conductor
EHV OHL Conductor (Tower Lines) | 66kV OHL (Tower Line) Conductor
EHV OHL Support - Towers | 33kV Tower
EHV OHL Support - Towers | 66kV Tower
EHV UG Cable (Gas) | 33kV UG Cable (Gas)
EHV UG Cable (Gas) | 66kV UG Cable (Gas)
EHV UG Cable (Non Pressurised) | 33kV UG Cable (Non Pressurised)
EHV UG Cable (Non Pressurised) | 66kV UG Cable (Non Pressurised)
EHV UG Cable (Oil) | 33kV UG Cable (Oil)
EHV UG Cable (Oil) | 66kV UG Cable (Oil)
Submarine Cables | HV Sub Cable
Submarine Cables | EHV Sub Cable
Submarine Cables | 132kV Sub Cable
EHV Switchgear (GM) | 33kV CB (Air Insulated Busbars)(ID) (GM)
EHV Switchgear (GM) | 33kV CB (Air Insulated Busbars)(OD) (GM)
EHV Switchgear (GM) | 33kV CB (Gas Insulated Busbars)(ID) (GM)
EHV Switchgear (GM) | 33kV CB (Gas Insulated Busbars)(OD) (GM)
EHV Switchgear (GM) | 33kV RMU
EHV Switchgear (GM) | 33kV Switch (GM)
EHV Switchgear (GM) | 66kV CB (Air Insulated Busbars)(ID) (GM)
EHV Switchgear (GM) | 66kV CB (Air Insulated Busbars)(OD) (GM)
EHV Switchgear (GM) | 66kV CB (Gas Insulated Busbars)(ID) (GM)
EHV Switchgear (GM) | 66kV CB (Gas Insulated Busbars)(OD) (GM)
EHV Transformer | 33kV Transformer (GM)
EHV Transformer | Transformador 34kV (GM)
EHV Transformer | 66kV Transformer (GM)
132kV OHL Fittings | 132kV Fittings
132kV OHL Conductor (Tower Lines) | 132kV OHL (Tower Line) Conductor
132kV OHL Support - Tower | 132kV Tower
132kV UG Cable (Gas) | 132kV UG Cable (Gas)
132kV UG Cable (Non Pressurised) | 132kV UG Cable (Non Pressurised)
132kV UG Cable (Oil) | 132kV UG Cable (Oil)
132kV CBs | 132kV CB (Air Insulated Busbars)(ID) (GM)
132kV CBs | 132kV CB (Air Insulated Busbars)(OD) (GM)
132kV CBs | 132kV CB (Gas Insulated Busbars)(ID) (GM)
132kV CBs | 132kV CB (Gas Insulated Busbars)(OD) (GM)
132kV Transformer | 132kV Transformer (GM)

## 2
Generic Term | Generic Term | Health Index Asset Category
Cable | Pressurised Cable | EHV UG Cable (Oil)
Cable | Pressurised Cable | EHV UG Cable (Gas)
Cable | Pressurised Cable | 132kV UG Cable (Oil)
Cable | Pressurised Cable | 132kV UG Cable (Gas)
Cable | Non Pressurised Cable | EHV UG Cable (Non Pressurised)
Cable | Non Pressurised Cable | 132kV UG Cable (Non Pressurised)
Cable | Non Pressurised Cable | Submarine Cables
Switchgear |  | LV Switchgear and Other
Switchgear |  | LV UGB
Switchgear |  | HV Switchgear (GM) - Distribution
Switchgear |  | HV Switchgear (GM) - Primary
Switchgear |  | EHV Switchgear (GM)
Switchgear |  | 132kV CBs
Transformers | HV Transformer | HV Transformer (GM)
Transformers | Grid & Primary (or EHV & 132kV) Transformers | EHV Transformer
Transformers | Grid & Primary (or EHV & 132kV) Transformers | 132kV Transformer
Overhead Line | Poles | LV OHL Support
Overhead Line | Poles | EHV OHL Support - Poles
Overhead Line | Poles | HV OHL Support - Poles
Overhead Line | Towers | EHV OHL Support - Towers
Overhead Line | Towers | 132kV OHL Support - Towers
Overhead Line | Fittings | EHV OHL Fittings
Overhead Line | Fittings | 132kV OHL Fittings
Overhead Line | OHL Conductor | EHV OHL Conductor (Tower Lines)
Overhead Line | OHL Conductor | 132kV OHL Conductor (Tower Lines)

## 3
Asset Register Category | Voltage
LV Main (OHL) Conductor | LV
LV Service (OHL) | LV
LV Main (UG Consac) | LV
LV Main (UG Plastic) | LV
LV Main (UG Paper) | LV
Rising & Lateral Mains | LV
LV Service (UG) | LV
LV Service associated with RLM | LV
Cut Out (Metered) | LV
LV Transformers/Regulators | LV
6.6/11kV OHL (Conventional Conductor) | HV
6.6/11kV OHL (BLX or similar Conductor) | HV
20kV OHL (Conventional Conductor) | HV
20kV OHL (BLX or similar Conductor) | HV
6.6/11kV UG Cable | HV
20kV UG Cable | HV
6.6/11kV CB (PM) | HV
6.6/11kV Switch (PM) | HV
6.6/11kV Switchgear - Other (PM) | HV
20kV CB (PM) | HV
20kV Switch (PM) | HV
20kV Switchgear - Other (PM) | HV
6.6/11kV Transformer (PM) | HV
20kV Transformer (PM) | HV
Batteries at GM HV Substations | HV
33kV OHL (Pole Line) Conductor | EHV
66kV OHL (Pole Line) Conductor | EHV
33kV Switchgear - Other | EHV
33kV Switch (PM) | EHV
66kV Switchgear - Other | EHV
33kV Transformer (PM) | EHV
Batteries at 33kV Substations | EHV
Batteries at 66kV Substations | EHV
132kV OHL (Pole Line) Conductor | 132kV
132kV Pole | 132kV
132kV Switchgear - Other | 132kV
Batteries at 132kV Substations | 132kV
Pilot Wire Overhead | Other
Pilot Wire Underground | Other
Cable Tunnel (DNO owned) | Other
Cable Bridge (DNO owned) | Other
Electrical Energy Storage | Other

## 4
Functional Failure Type | Description
Catastrophic | A sudden and total failure from which recovery of the asset (and or sub component) is not feasible.
Degraded | A significant failure associated with advanced degradation.
Incipient | A minor failure associated with early stage degradation

## 5
Health Index Band | Lower | Upper | Bound Description
HI1 | 0.5 | 3 | Limit of Health Score
HI2 | 3 | 5.5 | Limit of Health Score
HI3 | 5.5 | 6.5 | Limit of Health Score
HI4 | 6.5 | 8 | Limit of Health Score
HI5 | 8 | 15 | Limit of Health Score

## 6
Criticality Index Band | Lower | Upper | Bound Description
C1 | 0 | 75 | Overall CoF (as % of Average Overall CoF for the Asset Category)
C2 | 75 | 125 | Overall CoF (as % of Average Overall CoF for the Asset Category)
C3 | 125 | 200 | Overall CoF (as % of Average Overall CoF for the Asset Category)
C4 | 200 |  | Overall CoF (as % of Average Overall CoF for the Asset Category)

## 7
Health Index Band | HEALTH SCORE USED TO DERIVE TYPICAL POF
HI1 | 1.23
HI2 | 4.25
HI3 | 6
HI4 | 7.25
HI5 | 9

## 8A
Criticality Index Band | Percentage Factor to Be Applied to The Reference Costs of Failure
C1 | 70%
C2 | 100%
C3 | 150%
C4 | 250%

## 8
Asset Category | Duty Factor 1 (DF1) | Duty Factor 2 (DF2)
Cables | % Utilisation | Operating Voltage ÷ Design Voltage
Poles | No asset-specific Duty Factor 1 (i.e. DF1 = 1) | N/A
LV UGB | No asset-specific Duty Factor 1 (i.e. DF1 = 1) | N/A
Switchgear - LV | No asset-specific Duty Factor 1 (i.e. DF1 = 1) | N/A
Switchgear - HV Distribution | No asset-specific Duty Factor 1 (i.e. DF1 = 1) | N/A
Switchgear - HV Primary | Number of Operations | N/A
Switchgear - EHV & 132kV | Number of Operations | N/A
Steel Tower | No asset-specific Duty Factor 1 (i.e. DF1 = 1) | N/A
Conductor | No asset-specific Duty Factor 1 (i.e. DF1 = 1) | N/A
Fittings | No asset-specific Duty Factor 1 (i.e. DF1 = 1) | N/A
HV Transformer (GM) | % Utilisation | N/A
HV Transformer (GM) | Transformer: % Utilisation | N/A
Transformers - EHV & 132kV | Tapchanger: Average Number of Daily Tapping Operations | N/A

## 9
a = Maximum of (Observed Condition Factor, Measured Condition Factor) | b = Minimum of (Observed Condition Factor, Measured Condition Factor) | Health Score Factor
>1 | >1 | = a + ((b-1)/1.5)
>1 | ≤1 | = a
≤1 | ≤1 | = b + ((a-1)/1.5)

## 10
Parameters for Combination Using MMI Technique - Factor Divider 1 | Parameters for Combination Using MMI Technique - Factor Divider 2 | Parameters for Combination Using MMI Technique - Max. No. of Condition Factors
1.5 | 1.5 | 4

## 11
Parameters for Combination Using MMI Technique - Factor Divider 1 | Parameters for Combination Using MMI Technique - Factor Divider 2 | Parameters for Combination Using MMI Technique - Max. No. of Condition Factors
1.5 | 1.5 | 2

## 12
Asset Category | Subcomponent | Observed Condition Input
LV UGB | N/A | 1. Steel Cover and Pit condition, 2. Water/Moisture, 3. Bell Condition, 4. Insulation Condition, 5. Signs of heating, 6. Phase Barriers
LV Circuit Breaker | N/A | 1. Switchgear external condition
LV Board (WM) | N/A | 1. Switchgear external condition, 2. Compound Leaks, 3. Switchgear internal condition, 4. Insulation, 5. Signs of Heating, 6. Phase Barriers
LV Pillars | N/A | 1. Switchgear external condition, 2. Compound Leaks, 3. Switchgear internal condition, 4. Insulation, 5. Signs of Heating, 6. Phase Barriers
HV Switchgear (GM) - Primary | N/A | 1. Switchgear external condition, 2. Cable boxes conditions, 3. Oil leaks/ Gas pressure, 4. Thermographic Assessment, 5. Switchgear internal condition and operation, 6. Indoor Environment
HV Switchgear (GM) - Distribution | N/A | 1. Switchgear external condition, 2. Cable boxes conditions, 3. Oil leaks/ Gas pressure, 4. Thermographic Assessment, 5. Switchgear internal condition and operation, 6. Indoor Environment
EHV Switchgear (GM) | N/A | 1. Switchgear external condition, 2. Cable boxes conditions, 3. Oil leaks/ Gas pressure, 4. Thermographic Assessment, 5. Switchgear internal condition and operation, 6. Indoor Environment, 7. Support Structures
132kV Switchgear (GM) | N/A | 1. Switchgear external condition, 2. Cable boxes conditions, 3. Oil leaks/ Gas pressure, 4. Thermographic Assessment, 5. Switchgear internal condition and operation, 6. Indoor Environment, 7. Support Structures, 8. Air systems
HV Transformer (GM) | N/A | 1. Transformer external condition, 2. Cabel boxes condition
EHV Transformer (GM) | Main Transformer | 1. Main tank condition, 2. Coolers/Radiator condition 3. Bushings condition 4. Kiosk condition 5. Cable boxes condition
EHV Transformer (GM) | Tapchanger | 1. Tapchanger external condition, 2. Internal Condition, 3. Drive Mechanism Condition, 4. Condition of Selector & Diverter Contacts, 5. Condition of Selector & Diverter Braids
132kV Transformer (GM) | Main Transformer | 1. Main tank condition, 2. Coolers/Radiator condition 3. Bushings condition 4. Kiosk condition 5. Cable boxes condition
132kV Transformer (GM) | Tapchanger | 1. Tapchanger external condition, 2. Internal Condition, 3. Drive Mechanism Condition, 4. Condition of Selector & Diverter Contacts, 5. Condition of Selector & Diverter Braids
EHV Cable (Non Pressurised) | N/A | None
EHV Cable (Oil) | N/A | 1. Presence of Crystalline Lead
EHV Cable (Gas) | N/A | 1. Presence of Crystalline Lead
132kV Cable (Non Pressurised) | N/A | None
132kV Cable (Oil) | N/A | 1. Presence of Crystalline Lead
132kV Cable (Gas) | N/A | 1. Presence of Crystalline Lead
Submarine Cable | N/A | 1. External Condition of Armour
LV Poles | N/A | 1. Visual Pole Condition, 2. Pole Top Rot, 3. Pole Leaning, 4. Bird / Animal Damage
HV Poles | N/A | 1. Visual Pole Condition, 2. Pole Top Rot, 3. Pole Leaning, 4. Bird / Animal Damage
EHV Poles | N/A | 1. Visual Pole Condition, 2. Pole Top Rot, 3. Pole Leaning, 4. Bird / Animal Damage
EHV Towers | Tower Steelwork | 1. Tower Legs, 2. Bracings, 3. Crossarms, 4. Peak
EHV Towers | Tower Paintwork | 1. Paintwork Condition
EHV Towers | Foundations | 1. Foundation Condition
132kV Towers | Tower Steelwork | 1. Tower Legs, 2. Bracings, 3. Crossarms, 4. Peak
132kV Towers | Tower Paintwork | 1. Paintwork Condition
132kV Towers | Foundations | 1. Foundation Condition
EHV Fittings | N/A | 1. Tower fittings, 2. Conductor fittings, 3. Insulators - Electrical, 4. Insulators - Mechanical
132kV Fittings | N/A | 1. Tower fittings, 2. Conductor fittings, 3. Insulators - Electrical, 4. Insulators - Mechanical
EHV Tower Line Conductor | N/A | 1. Visual Condition, 2. Midspan joints
132kV Tower Line Conductor | N/A | 1. Visual Condition, 2. Midspan joints

## 13
Asset Category | Subcomponent | Parameters for Combination Using MMI Technique - Factor Divider 1 | Parameters for Combination Using MMI Technique - Factor Divider 2 | Parameters for Combination Using MMI Technique - Max. No. of Combined Factors
LV UGB | N/A | 1.5 | 1.5 | 3
LV Circuit Breaker | N/A | 1.5 | 1.5 | 1
LV Board (WM) | N/A | 1.5 | 1.5 | 3
LV Pillars | N/A | 1.5 | 1.5 | 3
HV Switchgear (GM) - Primary | N/A | 1.5 | 1.5 | 3
HV Switchgear (GM) - Distribution | N/A | 1.5 | 1.5 | 3
EHV Switchgear (GM) | N/A | 1.5 | 1.5 | 3
132kV Switchgear (GM) | N/A | 1.5 | 1.5 | 3
HV Transformer (GM) | N/A | 1.5 | 1.5 | 2
EHV Transformer (GM) | Main Transformer | 1.5 | 1.5 | 3
EHV Transformer (GM) | Tapchanger | 1.5 | 1.5 | 3
132kV Transformer (GM) | Main Transformer | 1.5 | 1.5 | 3
132kV Transformer (GM) | Tapchanger | 1.5 | 1.5 | 3
Submarine Cable | N/A | 1.5 | 1.5 | 1
LV Poles | N/A | 1.5 | 1.5 | 2
HV Poles | N/A | 1.5 | 1.5 | 2
EHV Poles | N/A | 1.5 | 1.5 | 2
EHV Towers | Tower Steelwork | 1.5 | 1.5 | 3
EHV Towers | Tower Paintwork | 1.5 | 1.5 | 1
EHV Towers | Foundations | 1.5 | 1.5 | 1
132kV Towers | Tower Steelwork | 1.5 | 1.5 | 3
132kV Towers | Tower Paintwork | 1.5 | 1.5 | 1
132kV Towers | Foundations | 1.5 | 1.5 | 1
EHV Fittings | N/A | 1.5 | 1.5 | 3
132kV Fittings | N/A | 1.5 | 1.5 | 3
EHV Tower Line Conductor | N/A | 1.5 | 1.5 | 1
132kV Tower Line Conductor | N/A | 1.5 | 1.5 | 1
EHV Cable (Non Pressurised) | N/A | N/A | N/A | N/A
EHV Cable (Oil) | N/A | 1.5 | 1.5 | 1
EHV Cable (Gas) | N/A | 1.5 | 1.5 | 1
132kV Cable (Non Pressurised) | N/A | N/A | N/A | N/A
132kV Cable (Oil) | N/A | 1.5 | 1.5 | 1
132kV Cable (Gas) | N/A | 1.5 | 1.5 | 1

## 14
Asset Category | Subcomponent | Measured Condition Input
LV UGB | N/A | 1. Operational Adequacy
LV Circuit Breaker | N/A | 1. Operational Adequacy
LV Board (WM) | N/A | 1. Operational Adequacy, 2. Security
LV Pillars | N/A | 1. Operational Adequacy
HV Switchgear (GM) - Primary | N/A | 1. Partial Discharge, 2. Ductor Test, 3. IR Test, 4. Oil Tests, 5. Temperature Readings, 6. Trip Test
HV Switchgear (GM) - Distribution | N/A | 1. Partial Discharge, 2. Ductor Test, 3. Oil Tests, 4. Temperature Readings, 5. Trip Test
EHV Switchgear (GM) | N/A | 1. Partial Discharge, 2. Ductor Test, 3. IR Test, 4. Oil Tests/ Gas Tests, 5. Temperature Readings, 6. Trip Test
132kV Switchgear (GM) | N/A | 1. Partial Discharge, 2. Ductor Test, 3. IR Test, 4. Oil Tests/ Gas Tests, 5. Temperature Readings, 6. Trip Test
HV Transformer (GM) | N/A | 1. Partial Discharge, 2. Temperature Readings
EHV Transformer (GM) | Main Transformer | 1. Partial Discharge, 2. Temperature Readings
EHV Transformer (GM) | Tapchanger | 1. Tapchanger Partial Discharge
132kV Transformer | Main Transformer | 1. Partial Discharge 2. Temperature Readings
132kV Transformer | Tapchanger | 1. Tapchanger Partial Discharge
EHV Cable (Non Pressurised) | N/A | 1. Sheath Test, 2. Partial Discharge, 3. Fault history
EHV Cable (Oil) | N/A | 1. Leakage
EHV Cable (Gas) | N/A | 1. Leakage
132kV Cable (Non Pressurised) | N/A | 1. Sheath Test, 2. Partial Discharge, 3. Fault history
132kV Cable (Oil) | N/A | 1. Leakage
132kV Cable (Gas) | N/A | 1. Leakage
Submarine Cable | N/A | 1. Sheath Test, 2. Partial Discharge, 3. Fault history
LV Poles | N/A | 1. Pole decay / deterioration
HV Poles | N/A | 1. Pole decay / deterioration
EHV Poles | N/A | 1. Pole decay / deterioration
EHV Towers | Tower Steelwork | None
EHV Towers | Tower Paintwork | None
EHV Towers | Foundations | None
132kV Towers | Tower Steelwork | None
132kV Towers | Tower Paintwork | None
132kV Towers | Foundations | None
EHV Fittings | N/A | 1. Thermal Imaging, 2. Ductor Tests
132kV Fittings | N/A | 1. Thermal Imaging, 2. Ductor Tests
EHV Tower Line Conductor | N/A | 1. Conductor Sampling, 2. Corrosion Monitoring Survey
132kV Tower Line Conductor | N/A | 1. Conductor Sampling, 2. Corrosion Monitoring Survey

## 15
Asset Category | Subcomponent | Parameters for Combination Using MMI Technique - Factor Divider 1 | Parameters for Combination Using MMI Technique - Factor Divider 2 | Parameters for Combination Using MMI Technique - Max. No. of Combined Factors
LV UGB | N/A | 1.5 | 1.5 | 1
LV Circuit Breaker | N/A | 1.5 | 1.5 | 1
LV Board (WM) | N/A | 1.5 | 1.5 | 1
LV Pillars | N/A | 1.5 | 1.5 | 1
HV Switchgear (GM) - Primary | N/A | 1.5 | 1.5 | 3
HV Switchgear (GM) - Distribution | N/A | 1.5 | 1.5 | 3
EHV Switchgear (GM) | N/A | 1.5 | 1.5 | 3
132kV Switchgear (GM) | N/A | 1.5 | 1.5 | 3
HV Transformer (GM) | N/A | 1.5 | 1.5 | 2
EHV Transformer (GM) | Main Transformer | 1.5 | 1.5 | 2
EHV Transformer (GM) | Tapchanger | 1.5 | 1.5 | 1
132kV Transformer (GM) | Main Transformer | 1.5 | 1.5 | 2
132kV Transformer (GM) | Tapchanger | 1.5 | 1.5 | 1
EHV Cable (Non Pressurised) | N/A | 1.5 | 1.5 | 2
EHV Cable (Oil) | N/A | 1.5 | 1.5 | 1
EHV Cable (Gas) | N/A | 1.5 | 1.5 | 1
132kV Cable (Non Pressurised) | N/A | 1.5 | 1.5 | 2
132kV Cable (Oil) | N/A | 1.5 | 1.5 | 1
132kV Cable (Gas) | N/A | 1.5 | 1.5 | 1
Submarine Cable | N/A | 1.5 | 1.5 | 2
LV Poles | N/A | 1.5 | 1.5 | 1
HV Poles | N/A | 1.5 | 1.5 | 1
EHV Poles | N/A | 1.5 | 1.5 | 1
EHV Fittings | N/A | 1.5 | 1.5 | 1
132kV Fittings | N/A | 1.5 | 1.5 | 1
EHV Tower Line Conductor | N/A | 1.5 | 1.5 | 1
132kV Tower Line Conductor | N/A | 1.5 | 1.5 | 1
EHV Towers | Tower Steelwork | N/A | N/A | N/A
EHV Towers | Tower Paintwork | N/A | N/A | N/A
EHV Towers | Foundations | N/A | N/A | N/A
132kV Towers | Tower Steelwork | N/A | N/A | N/A
132kV Towers | Tower Paintwork | N/A | N/A | N/A
132kV Towers | Foundations | N/A | N/A | N/A

## 16
Asset Register Category | Financial - (GBP) | Safety - (GBP) | Environmental - (GBP) | Network Performance - (GBP) | Total - (GBP)
LV Poles | 1337 | 601 | 90 | 542 | 2570
6.6/11kV Poles | 1913 | 200 | 90 | 1930 | 4133
20kV Poles | 2295 | 200 | 90 | 1930 | 4515
33kV Pole | 2466 | 200 | 90 | 92 | 2947
66kV Pole | 3718 | 200 | 90 | 183 | 4191
33kV Tower | 6749 | 377 | 186 | 580 | 7893
66kV Tower | 12647 | 377 | 186 | 1663 | 14873
132kV Tower | 14623 | 377 | 186 | 4157 | 19343
33kV Fittings | 227 | 1508 | 96 | 267 | 2098
66kV Fittings | 292 | 1508 | 96 | 533 | 2429
132kV Fittings | 485 | 1508 | 96 | 1333 | 3423
33kV OHL (Tower Line) Conductor | 17793 | 1508 | 96 | 1333 | 20731
66kV OHL (Tower Line) Conductor | 23600 | 1508 | 96 | 2667 | 27871
132kV OHL (Tower Line) Conductor | 20408 | 1508 | 96 | 6667 | 28680
HV Sub Cable | 181996 | 2 | 3600 | 190344 | 375942
33kV UG Cable (Non Pressurised) | 31644 | 2 | 726 | 3530 | 35901
33kV UG Cable (Oil) | 129 | 2 | 5885 | 4 | 6019
33kV UG Cable (Gas) | 317 | 2 | 54 | 35 | 407
66kV UG Cable (Non Pressurised) | 64021 | 2 | 726 | 7059 | 71808
66kV UG Cable (Oil) | 140 | 2 | 5885 | 7 | 6033
66kV UG Cable (Gas) | 519 | 2 | 54 | 71 | 645
132kV UG Cable (Non Pressurised) | 109244 | 2 | 1086 | 17684 | 127980
132kV UG Cable (Oil) | 154 | 2 | 7410 | 18 | 7583
132kV UG Cable (Gas) | 802 | 2 | 81 | 176 | 1060
EHV Sub Cable | 285322 | 2 | 3600 | 3530 | 292453
132kV Sub Cable | 480542 | 2 | 3600 | 17648 | 501792
LV Circuit Breaker | 4070 | 9109 | 22 | 11085 | 24285
LV Pillar (ID) | 5669 | 9109 | 22 | 8243 | 23543
LV Pillar (OD at Substation) | 6170 | 9109 | 22 | 8243 | 23543
LV Pillar (OD not at a Substation) | 3429 | 9622 | 22 | 8243 | 21316
LV UGB | 3429 | 9622 | 85 | 2748 | 15884
LV Board (WM) | 7833 | 9109 | 22 | 8243 | 25206
LV Board (X-type Network) (WM) | 9244 | 9109 | 22 | 8243 | 26617
6.6/11kV CB (GM) Primary | 7586 | 23502 | 1547 | 40530 | 73165
6.6/11kV CB (GM) Secondary | 8000 | 4823 | 1486 | 11580 | 24848
6.6/11kV Switch (GM) | 5267 | 4823 | 1486 | 11580 | 23156
6.6/11kV RMU | 9839 | 4823 | 1486 | 11580 | 27728
6.6/11kV X-type RMU | 13314 | 4823 | 1486 | 11580 | 31203
20kV CB (GM) Primary | 9504 | 23502 | 1547 | 40530 | 75082
20kV CB (GM) Secondary | 7214 | 4823 | 1486 | 11580 | 25103
20kV Switch (GM) | 6104 | 4823 | 1486 | 11580 | 23993
20kV RMU | 10024 | 4823 | 1486 | 11580 | 27912
33kV CB (Air Insulated Busbars)(ID) (GM) | 14513 | 23502 | 4356 | 29120 | 71490
33kV CB (Air Insulated Busbars)(OD) (GM) | 17870 | 23502 | 4356 | 14740 | 60467
33kV CB (Gas Insulated Busbars)(ID) (GM) | 21984 | 23502 | 4356 | 29120 | 78961
33kV CB (Gas Insulated Busbars)(OD) (GM) | 21984 | 23502 | 4356 | 14740 | 64581
33kV Switch (GM) | 10257 | 23502 | 4356 | 14740 | 52854
33kV RMU | 25347 | 23502 | 4356 | 14740 | 67944
66kV CB (Air Insulated Busbars)(ID) (GM) | 28930 | 23502 | 4356 | 29120 | 85907
66kV CB (Air Insulated Busbars)(OD) (GM) | 46252 | 23502 | 4356 | 14740 | 88849
66kV CB (Gas Insulated Busbars)(ID) (GM) | 52176 | 23502 | 4356 | 29120 | 109153
66kV CB (Gas Insulated Busbars)(OD) (GM) | 52176 | 23502 | 4356 | 14740 | 94773
132kV CB (Air Insulated Busbars)(ID) (GM) | 81092 | 36171 | 21756 | 153867 | 292866
132kV CB (Air Insulated Busbars)(OD) (GM) | 38181 | 36171 | 21756 | 38826 | 134934
132kV CB (Gas Insulated Busbars)(ID) (GM) | 168892 | 36171 | 21756 | 153867 | 380686
132kV CB (Gas Insulated Busbars)(OD) (GM) | 168892 | 36171 | 21756 | 38826 | 265645
6.6/11kV Transformer (GM) | 9297 | 4823 | 3809 | 4343 | 22271
20kV Transformer (GM) | 10585 | 4823 | 3809 | 4343 | 23560
33kV Transformer (GM) | 134796 | 23502 | 17048 | 28940 | 157188
Transformador 34kV (GM) | 134796 | 23502 | 17048 | 28940 | 157188
66kV Transformer (GM) | 263015 | 23502 | 17048 | 28940 | 204285
132kV Transformer (GM) | 218932 | 36171 | 35095 | 230441 | 564721

## 17
Fixed value | Source
Environmental cost per litre oil (GBP/litre) | This is derived from the EU trading value for carbon emissions and is consistent with the value used in Ofgem's RIIO-ED2 Cost Benefit Analysis template (used for the RIIO-ED2 submissions) (at 2020/21 prices)
Traded carbon price (GBP/t) | Traded carbon price for 2028 from central scenario in Department for Business, Energy & Industrial Strategy's published 'Updated Short-Term Traded Carbon Values used for UK public policy appraisal (2018)' document (inflated to 2020/21 prices) – see https://www.gov.uk/government/publications/updated-short-term-traded-carbon-valuesused-for-uk-policy-appraisal-2018
Conversion factor for cost of SF6 loss c/w cost of carbon (kg CO2e/kg) | 2011/12 Defra conversion factor

## 18
Lower | Upper | Bound Description | No. of Customers to be used in the derivation of Customer Factor
0 | 50 | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) | 1 x actual number of customers fed by the asset
50 | 100 | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) | 25 x actual number of customers fed by the asset
100 | 500 | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) | 100 x actual number of customers fed by the asset
500 | 1000 | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) | 250 x actual number of customers fed by the asset
1000 | 2000 | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) | 500 x actual number of customers fed by the asset
2000 |  | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) | 1000 x actual number of customers fed by the asset

## 19
Asset Category | Function | Failure modes | Catastrophic Failure | Degraded Failures | Incipient Failures | Functional failures excluded
LV Circuit Breaker | Measure and break unsafe levels of current (over current), make load current, and provide a point of electrical isolation. | Failing to open on a fault. Failing to close reliably. Failing to open during manual operation. Failure to supply load current (i.e. failure during normal operating conditions). Opens Spuriously under normal conditions. Opens Intermittently (Faulty). | Failure of Housing. Disruptive Failure Resulting from Insulation Breakdown. | Nuisance tripping or failure to operate when required due to: 1. damage to contacts 2. loose internal connections 3. Damage to mechanism and drive rods. | Nuisance tripping or failure to operate when required due to: - Maladjusted linkage. | Failure of protection module., Failure of SCADA.
LV Pillar (ID) | Provide a number of points of access to LV Cable Systems for electrical connection, isolation and flexibility with network reconfiguration. Depending on the complexity of pillar they may also offer monitoring and protection (fuse or circuit breaker) capabilities. | Failing to close reliably. Failing to open during manual operation. Failure to supply load current (i.e. failure during normal operating conditions). | Failure of Housing. Disruptive Failure Resulting from Insulation Breakdown requiring the replacement of one or all ways. | Failure of Housing requiring repair. Nuisance tripping or Failure of an LV Pillar's Fuse, MCB or RCBO to operate when required due to: 1. deteriorated fuse carriers 2. breaker stuck closed. | Nuisance tripping or Failure of an LV Pillar's Fuse, MCB or RCBO to operate when required due to: 1. incorrect fuse/breaker rating 2. breaker not latching closed. | Contact damage due to incorrect operation of board.
LV Pillar (OD at Substation / LV Pillar (OD not at a Substation) | Provide a number of points of access to LV Cable Systems for electrical connection, isolation and flexibility with network reconfiguration. Depending on the complexity of pillar they may also offer monitoring and protection (fuse or circuit breaker) capabilities. | Failing to close reliably. Failing to open during manual operation. Failure to supply load current (i.e. failure during normal operating conditions). | Failure of Housing. Disruptive Failure Resulting from Insulation Breakdown requiring the replacement of one or all ways. | Failure of Housing requiring repair. Nuisance tripping or Failure of an LV Pillar's Fuse, MCB or RCBO to operate when required due to: 1. deteriorated fuse carriers 2. breaker stuck closed. | Nuisance tripping or Failure of an LV Pillar's Fuse, MCB or RCBO to operate when required due to: 1. incorrect fuse/breaker rating 2. breaker not latching closed. | Contact damage due to incorrect operation of board.
LV Board (WM) | Provide a number of points of access to LV Cable Systems for electrical connection, isolation and flexibility with network reconfiguration. Depending on the complexity of LV Board, they may also offer monitoring and protection (fuse or circuit breaker) capabilities. | Failing to open on a fault. Failing to close reliably. Failing to open during manual operation. Failure to supply load current (i.e. failure during normal operating conditions). Opens Spuriously under normal conditions. Opens Intermittently (Faulty). | Disruptive Failure Resulting from Insulation Breakdown. | Nuisance tripping or failure to operate when required due to: 1. damage to contacts, 2. moisture ingress, 3. deteriorated fuse carriers. | Nuisance tripping or failure to operate when required due to: 1. damage to contacts, 2. loose internal connections, 3. failure of protection module. | Failure of housing. Contact Damage due to Incorrect operation of Board.
LV UGB | Provide a number of points of access to LV Cable Systems for electrical connection, isolation and flexibility with network reconfiguration. Depending on the complexity of the LV Box, they may also offer monitoring and protection (fuse or circuit breaker) capabilities. | Failing to open on a fault (if used in this mode. Failing to close reliably. Failing to open during manual operation. Failure to supply load current (i.e. failure during normal operating conditions). Opens Spuriously under normal conditions. Opens Intermittently (Faulty). | Disruptive Failure Resulting from Insulation Breakdown. | Failure to be operable when required due to: 1. damage to contacts, 2. moisture ingress, 3. deteriorated links. | Failure to be operable when required due to: 1. damage to contacts, 2. loose internal connections. | Failure of housing. Contact Damage due to Incorrect operation of Box.
HV Switchgear (GM) – Primary / HV Switchgear (GM) - Distribution | Carry, make or break continuous load or fault current. Maintain or interrupt voltage on all three phases. Isolation & Earthing of Cables & Plant. Measurement of current and voltage. | Does not open or close on command (Where this is associated with the Breaker and not the control system). , Mechanical Failure. , Electrical Failure (Auxiliary & Control). , Electrical Failure (Main Circuit). | Disruptive Failure Resulting from Insulation Breakdown. | SOP preventing operation. Failure to operate when required due to: 1. Failure of Mechanism, 2. Protection module, 3. CT Failure, 4. VT Failure, 5.Stuck Breaker. | Failure to operate when required due to: - Low Gas Lockout or Vacuum bottle condition. | Unable to withstand impulse voltage. Unable to contain the insulating medium. Does not allow switch tank to breath. Unable to support its own weight. Does not provide a connection to the substation earth mat.
EHV Switchgear (GM) | Carry, make or break continuous load or fault current. Maintain or interrupt voltage on all three phases. Isolation & Earthing of Cables & Plant. Measurement of current and voltage. | Does not open or close on command (Where this is associated with the Breaker and not the control system). Mechanical Failure. Electrical Failure (Auxiliary & Control). Electrical Failure (Main Circuit). | Disruptive Failure Resulting from Insulation Breakdown. | SOP preventing operation. Failure to operate when required due to: 1. Failure of Mechanism, 2. Protection module, 3. CT Failure, 4. VT Failure, 5. Stuck Breaker. | Failure to operate when required due to: - Low Gas Lockout or Vacuum bottle condition. | Unable to withstand impulse voltage. Unable to contain the insulating medium. Does not allow switch tank to breath. Unable to support its own weight. Does not provide a connection to the substation earth mat. Failure of civil structures or associated disconnectors. Any asset classed by RIG definition as EHV Swgr Other.
132kV CBs | Carry, make or break continuous load or fault current. Maintain or interrupt voltage on all three phases. Isolation & Earthing of Cables & Plant. Measurement of current and voltage. | Does not open or close on command (Where this is associated with the Breaker and not the control system). Mechanical Failure. Electrical Failure (Auxiliary & Control). Electrical Failure (Main Circuit). | Disruptive Failure Resulting from Insulation Breakdown. | SOP preventing operation. Failure to operate when required due to: 1. Failure of Mechanism, 2. Protection module, 3. CT Failure, 4. VT Failure, 5. Stuck Breaker. | Failure to operate when required due to: - Low Gas Lockout or Vacuum bottle condition. | Unable to withstand impulse voltage. Unable to contain the insulating medium. Does not allow switch tank to breath. Unable to support its own weight. Does not provide a connection to the substation earth mat. Failure of civil structures or associated disconnectors. Any asset classed by RIG definition as EHV Swgr Other.
HV Transformer (GM) | Step up or step down and provide a secondary output voltage which is within statutory limits. Carry full load current when required. Carry through fault current when required. | Tapchanger, bushing, windings, core, tank or insulation failure. | Failure of the main internal components - windings, core or insulation. | Failure of the bushing, cable termination, including box and conservator tank. | Failure of the Tapchanger. | Oil condition corrected by an oil change and not re-conditioning, levels and leaks. Cable connection to controlling switchgear. Civil structure related failures
EHV Transformer / 132kV Transformer | Step up or step down and provide a secondary output voltage which is within statutory limits. Carry full load current when required. Carry through fault current when required. | Tapchanger, bushing, windings, core, tank, insulation or control/monitoring failure. | Failure of the tank or main internal components - windings, core or insulation. | Failure of the bushing, cable termination conservator tank and associated radiator. | Failure of the Tapchanger. | Oil condition corrected by an oil change and not re-conditioning, levels and leaks. CT's, VT's and on tank unit auxiliary transformers associated with the unit NER's and NEX's Neutral displacement VT's. Cable and busbar connection to controlling switchgear. Civil structure related failures. Buchholz.
Poles | Support electrical equipment in compliance with the ESQCR and Construction Regulations. | Decayed Pole. Decayed Struts. Snapped Stays. | Any structure whose components have either failed (broken) or whose residual strength has decreased to a level where immediate replacement of all or part of the structure is required. | Any structure whose components have a residual strength such that replacement is required within the timescale defined by the Company. | Vermin Damage resulting in Factor of Safety reduction requiring an intervention. | Broken Conductor. Broken or damaged fittings. Damaged or non-functioning plant. Broken or damaged insulation. Missing or degraded safety signs and anti climbing fixtures. Leaning poles where statutory clearances are not impacted. Cable boxes and platforms, including sealing ends.
Towers | Support electrical equipment in compliance with the ESQCR. | Corrosion or distortion of the structure, i.e. bent member, failing foundations. | Any structure whose components have either failed (broken) or whose residual strength has decreased to a level where immediate replacement of all or part of the structure is required. | Any component of the structure who's condition is such that it prevents normal operation of the Tower, or degrades the residual strength of the Tower, requiring an intervention with in a defined period. | Corrosion to minor Tower components and land movements degrading the potential of the Towers stability. | Broken Conductor. Broken or damaged fittings. Broken or damaged insulation. Missing or degraded safety signs and anti-climbing fixtures. Cable boxes and platforms, including sealing ends.
Fittings / OHL Conductor | Carry load and fault current without annealing or sagging below the ESQCR limit. Maintain continuity under normal and fault conditions. Provide phase-phase and phase-earth insulation. | Flashover. Insulation failure. Corroded Conductor. Corroded Jumper. Corroded Fitting. | Loss of structural integrity of any component associated with an overhead line supported on Steel Tower, excluding any associated Tower mounted plant, such that the residual strength of the component required immediate intervention. | Loss of structural integrity of any component associated with an overhead line supported on the Tower, excluding any associated Tower mounted plant, such that the residual strength of the component required intervention within a prescribed timescale. | Cracked insulator | Loss of protection. Loss of plant. Earthing. Any issues relating to the support, safety notices and anti-climbing guards. Conductor icing which does not result in permanent damage to the conductor. Cable boxes and platforms (including sealing ends).
Pressurised Cable | Carry load and fault current safely and reliably, without overheating or causing damage to the environment. | Oil or Gas leak / Top up. Cable Fault. Joint Failure. | Cable Fault. Joint Fault. | Accessory or joint failure causing loss of fluid. | Pressure gauges. Sheath deterioration. | Sheath damage and or repair. Third party damages.
Submarine Cables | Carry load and fault current safely and reliably, without overheating or causing damage to the environment. | Cable Fault. Joint Failure. | Cable Fault. Joint Fault. | N/A | N/A | Sheath damage and or repair. Third party damages
Non Pressurised Cable | Carry load and fault current safely and reliably, without overheating or causing damage to the environment. | Cable fault. Joint failure. | Cable Fault. Joint Fault. | N/A | N/A | Sheath damage and or repair. Third party damages.
Concrete Structures | Carries a piece of switchgear and is an integral part of the plant. This excludes plinths for plant which is designed with legs or other types of support for the operable parts of the plant and all power transformers. | Loss of residual strength or loss of stability. | Failure of the structure resulting in the plant item becoming unstable, the plant tilts or in any other way cannot be operated as a result of the condition of the concrete. | Loss of section. Cracking and spilling of the concrete such that the residual strength is between 80 and 100% of current condition. | Loss of chemical structure and hence reduction in strength. | Plinths. Auxiliary structures not made of concrete. Busbar supports.

## 20
Asset Register Category | Sub-division | Normal Expected Life
LV Poles | Concrete | 60
LV Poles | Steel | 50
LV Poles | Wood (water soluble copper salt treated; excluding CCA) | 25
LV Poles | Wood | 55
LV Poles | Other (e.g. fibreglass) | 80
LV Circuit Breaker |  | 60
LV Pillar (ID) |  | 60
LV Pillar (OD at Substation) |  | 60
LV Pillar (OD not at a Substation) |  | 60
LV Board (WM) |  | 60
LV UGB |  | 55
LV Board (X-type Network) (WM) |  | 60
6.6/11kV Poles | Concrete | 60
6.6/11kV Poles | Steel | 50
6.6/11kV Poles | Wood (water soluble copper salt treated; excluding CCA) | 25
6.6/11kV Poles | Wood | 55
6.6/11kV Poles | Other (e.g. fibreglass) | 80
20kV Poles | Concrete | 60
20kV Poles | Steel | 50
20kV Poles | Wood (water soluble copper salt treated; excluding CCA) | 25
20kV Poles | Wood | 55
20kV Poles | Other (e.g. fibreglass) | 80
HV Sub Cable |  | 60
6.6/11kV CB (GM) Primary |  | 55
6.6/11kV CB (GM) Secondary |  | 55
6.6/11kV Switch (GM) |  | 55
6.6/11kV RMU |  | 55
6.6/11kV X-type RMU |  | 55
20kV CB (GM) Primary |  | 55
20kV CB (GM) Secondary |  | 55
20kV Switch (GM) |  | 55
20kV RMU |  | 55
6.6/11kV Transformer (GM) |  | 60
20kV Transformer (GM) |  | 60
33kV Pole | Concrete | 60
33kV Pole | Steel | 50
33kV Pole | Wood (water soluble copper salt treated; excluding CCA) | 25
33kV Pole | Wood | 55
33kV Pole | Other (e.g. fibreglass) | 80
66kV Pole | Concrete | 60
66kV Pole | Steel | 50
66kV Pole | Wood (water soluble copper salt treated; excluding CCA) | 25
66kV Pole | Wood | 55
66kV Pole | Other (e.g. fibreglass) | 80
33kV OHL (Tower Line) Conductor | ACSR - greased | 55
33kV OHL (Tower Line) Conductor | ACSR - non-greased | 50
33kV OHL (Tower Line) Conductor | AAAC | 60
33kV OHL (Tower Line) Conductor | Cad Cu | 50
33kV OHL (Tower Line) Conductor | Cu | 70
33kV OHL (Tower Line) Conductor | Other | 50
33kV Tower | Steelwork | 80
33kV Tower | Foundation - Fully Encased Concrete | 95
33kV Tower | Foundation - Earth Grillage | 60
33kV Tower | Paint System - Galvanising | 30
33kV Tower | Paint System - Paint | 20
33kV Fittings |  | 40
66kV OHL (Tower Line) Conductor | ACSR - greased | 55
66kV OHL (Tower Line) Conductor | ACSR - non-greased | 50
66kV OHL (Tower Line) Conductor | AAAC | 60
66kV OHL (Tower Line) Conductor | Cad Cu | 50
66kV OHL (Tower Line) Conductor | Cu | 70
66kV OHL (Tower Line) Conductor | Other | 50
66kV Tower | Steelwork | 80
66kV Tower | Foundation - Fully Encased Concrete | 95
66kV Tower | Foundation - Earth Grillage | 60
66kV Tower | Paint System - Galvanising | 30
66kV Tower | Paint System - Paint | 20
66kV Fittings |  | 40
33kV UG Cable (Non Pressurised) | Aluminium sheath - Aluminium conductor | 100
33kV UG Cable (Non Pressurised) | Aluminium sheath - Copper conductor | 100
33kV UG Cable (Non Pressurised) | Lead sheath - Aluminium conductor | 100
33kV UG Cable (Non Pressurised) | Lead sheath - Copper conductor | 100
33kV UG Cable (Oil) | Aluminium sheath - Aluminium conductor | 75
33kV UG Cable (Oil) | Aluminium sheath - Copper conductor | 75
33kV UG Cable (Oil) | Lead sheath - Aluminium conductor | 80
33kV UG Cable (Oil) | Lead sheath - Copper conductor | 80
33kV UG Cable (Gas) | Aluminium sheath - Aluminium conductor | 65
33kV UG Cable (Gas) | Aluminium sheath - Copper conductor | 70
33kV UG Cable (Gas) | Lead sheath - Aluminium conductor | 75
33kV UG Cable (Gas) | Lead sheath - Copper conductor | 75
66kV UG Cable (Non Pressurised) | Aluminium sheath - Aluminium conductor | 100
66kV UG Cable (Non Pressurised) | Aluminium sheath - Copper conductor | 100
66kV UG Cable (Non Pressurised) | Lead sheath - Aluminium conductor | 100
66kV UG Cable (Non Pressurised) | Lead sheath - Copper conductor | 100
66kV UG Cable (Oil) | Aluminium sheath - Aluminium conductor | 75
66kV UG Cable (Oil) | Aluminium sheath - Copper conductor | 75
66kV UG Cable (Oil) | Lead sheath - Aluminium conductor | 80
66kV UG Cable (Oil) | Lead sheath - Copper conductor | 80
66kV UG Cable (Gas) | Aluminium sheath - Aluminium conductor | 65
66kV UG Cable (Gas) | Aluminium sheath - Copper conductor | 70
66kV UG Cable (Gas) | Lead sheath - Aluminium conductor | 75
66kV UG Cable (Gas) | Lead sheath - Copper conductor | 75
EHV Sub Cable |  | 60
33kV CB (Air Insulated Busbars)(ID) (GM) |  | 60
33kV CB (Air Insulated Busbars)(OD) (GM) |  | 50
33kV CB (Gas Insulated Busbars)(ID)(GM) |  | 60
33kV CB (Gas Insulated Busbars)(OD)(GM) |  | 50
33kV Switch (GM) |  | 55
33kV RMU |  | 55
66kV CB (Air Insulated Busbars)(ID) (GM) |  | 50
66kV CB (Air Insulated Busbars)(OD) (GM) |  | 55
66kV CB (Gas Insulated Busbars)(ID)(GM) |  | 55
66kV CB (Gas Insulated Busbars)(OD)(GM) |  | 50
33kV Transformer (GM) | Transformer - Pre 1980 | 60
33kV Transformer (GM) | Transformer - Post 1980 | 50
Transformador 34kV (GM) | Transformer - Pre 1980 | 60
Transformador 34kV (GM) | Transformer - Post 1980 | 50
33kV Transformer (GM) | Tapchanger | 60
66kV Transformer (GM) | Transformer - Pre 1980 | 60
66kV Transformer (GM) | Transformer - Post 1980 | 50
66kV Transformer (GM) | Tapchanger | 60
132kV OHL (Tower Line) Conductor | ACSR - greased | 55
132kV OHL (Tower Line) Conductor | ACSR - non-greased | 50
132kV OHL (Tower Line) Conductor | AAAC | 60
132kV OHL (Tower Line) Conductor | Cad Cu | 50
132kV OHL (Tower Line) Conductor | Cu | 70
132kV OHL (Tower Line) Conductor | Other | 50
132kV Tower | Steelwork | 80
132kV Tower | Foundation - Fully Encased Concrete | 95
132kV Tower | Foundation - Earth Grillage | 60
132kV Tower | Paint System - Galvanising | 30
132kV Tower | Paint System - Paint | 20
132kV Fittings |  | 40
132kV UG Cable (Non Pressurised) | Aluminium sheath - Aluminium conductor | 100
132kV UG Cable (Non Pressurised) | Aluminium sheath - Copper conductor | 100
132kV UG Cable (Non Pressurised) | Lead sheath - Aluminium conductor | 100
132kV UG Cable (Non Pressurised) | Lead sheath - Copper conductor | 100
132kV UG Cable (Oil) | Aluminium sheath - Aluminium conductor | 75
132kV UG Cable (Oil) | Aluminium sheath - Copper conductor | 75
132kV UG Cable (Oil) | Lead sheath - Aluminium conductor | 80
132kV UG Cable (Oil) | Lead sheath - Copper conductor | 80
132kV UG Cable (Gas) | Aluminium sheath - Aluminium conductor | 65
132kV UG Cable (Gas) | Aluminium sheath - Copper conductor | 70
132kV UG Cable (Gas) | Lead sheath - Aluminium conductor | 75
132kV UG Cable (Gas) | Lead sheath - Copper conductor | 75
132kV Sub Cable |  | 60
132kV CB (Air Insulated Busbars)(ID) (GM) |  | 60
132kV CB (Air Insulated Busbars)(OD) (GM) |  | 50
132kV CB (Gas Insulated Busbars)(ID) (GM) |  | 60
132kV CB (Gas Insulated Busbars)(OD) (GM) |  | 55
132kV Transformer (GM) | Transformer - Pre 1980 | 60
132kV Transformer (GM) | Transformer - Post 1980 | 50
132kV Transformer (GM) | Tapchanger | 60

## 21
Functional Failure Category | K-Value (%) | C-Value | Health Score Limit
LV UGB | 0.0077 | 1.087 | 4
LV Circuit Breaker | 0.0041 | 1.087 | 4
LV Pillar (ID) | 0.0046 | 1.087 | 4
LV Pillar (OD at Substation) / LV Pillar (OD not at a Substation) | 0.0046 | 1.087 | 4
LV Board (WM) | 0.0069 | 1.087 | 4
HV Switchgear (GM) - Primary | 0.0052 | 1.087 | 4
HV Switchgear (GM) - Distribution (GM) | 0.0067 | 1.087 | 4
EHV Switchgear (GM) (33kV & 22kV assets only) | 0.0223 | 1.087 | 4
EHV Switchgear (GM) (66kV assets only) | 0.0512 | 1.087 | 4
132kV CBs | 0.0431 | 1.087 | 4
HV Transformer (GM) | 0.0078 | 1.087 | 4
EHV Transformer/ 132kV Transformer | 0.0454 | 1.087 | 4
Poles | 0.0285 | 1.087 | 4
Towers | 0.0545 | 1.087 | 4
Fittings | 0.0096 | 1.087 | 4
OHL Conductor | 0.008 | 1.087 | 4
Pressurised Cable (EHV UG Cable (Oil) and 132kV UG Cable (Oil)) | 2.0944 | 1.087 | 4
Pressurised Cable (EHV UG Cable (Gas) and 132kV UG Cable (Gas)) | 4.5036 | 1.087 | 4
Submarine Cables | 0.0202 | 1.087 | 4
Non Pressurised Cable | 0.0658 | 1.087 | 4

## 22
Lower | Upper | Bound Description | Switchgear | Transformers | Poles (Wood) | Poles (Steel) | Poles (Concrete) | Towers (Structure) | Towers (Fittings) | Towers (Conductor)
0 | 1 | Distance from Coast Banding (km) | 1.35 | 1.35 | 1 | 1.5 | 1.25 | 1.8 | 2 | 2
1 | 5 | Distance from Coast Banding (km) | 1.1 | 1.1 | 1 | 1.2 | 1.1 | 1.45 | 1.5 | 1.5
5 | 10 | Distance from Coast Banding (km) | 1.05 | 1.05 | 1 | 1.1 | 1.05 | 1.2 | 1.2 | 1.2
10 | 20 | Distance from Coast Banding (km) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
20 |  | Distance from Coast Banding (km) | 0.9 | 0.9 | 1 | 1 | 1 | 0.85 | 1 | 1
Default | Default | Distance from Coast Banding (km) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## 23
Lower | Upper | Bound Description | Switchgear | Transformers | Poles (Wood) | Poles (Steel) | Poles (Concrete) | Towers (Structure) | Towers (Fittings) | Towers (Conductor)
0 | 100 | Altitude From Sea Level Banding (m) | 0.9 | 0.9 | 1 | 1 | 1 | 0.9 | 0.95 | 0.95
100 | 200 | Altitude From Sea Level Banding (m) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
200 | 300 | Altitude From Sea Level Banding (m) | 1.05 | 1.05 | 1 | 1 | 1 | 1.15 | 1.05 | 1.05
300 |  | Altitude From Sea Level Banding (m) | 1.1 | 1.1 | 1 | 1 | 1 | 1.3 | 1.15 | 1.15
Default | Default | Altitude From Sea Level Banding (m) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## 24
Corrosion Category Index | Switchgear | Transformers | Poles (Wood) | Poles (Steel) | Poles (Concrete) | Towers (Structure) | Towers (Fittings) | Towers (Conductor)
1 | 0.9 | 0.9 | 1 | 0.9 | 0.9 | 0.75 | 0.95 | 0.95
2 | 0.95 | 0.95 | 1 | 0.95 | 0.95 | 0.9 | 0.95 | 0.95
3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
4 | 1.1 | 1.1 | 1 | 1.15 | 1.05 | 1.3 | 1.05 | 1.05
5 | 1.25 | 1.25 | 1 | 1.35 | 1.1 | 1.6 | 1.2 | 1.2
Default | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## 25
Increment Constant | Switchgear | Transformers | Submarine Cables | Poles (Wood) | Poles (Steel) | Poles (Concrete) | Towers (Structure) | Towers (Fittings) | Towers (Conductor)
INC | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0

## 26
Asset Register Category | Default 'environment' to be assumed when deriving Location Factor
LV Poles | Outdoor
LV Circuit Breaker | Indoor
LV Pillar (ID) | Indoor
LV Pillar (OD at Substation) | Outdoor
LV Pillar (OD not at a Substation) | Outdoor
LV Board (WM) | Indoor
LV UGB | n/a
LV Board (X-type Network) (WM) | Indoor
6.6/11kV Poles | Outdoor
20kV Poles | Outdoor
HV Sub Cable | n/a
6.6/11kV CB (GM) Primary | Indoor
6.6/11kV CB (GM) Secondary | Indoor
6.6/11kV Switch (GM) | Indoor
6.6/11kV RMU | Indoor
6.6/11kV X-type RMU | Indoor
20kV CB (GM) Primary | Indoor
20kV CB (GM) Secondary | Indoor
20kV Switch (GM) | Indoor
20kV RMU | Indoor
6.6/11kV Transformer (GM) | Indoor
20kV Transformer (GM) | Indoor
33kV Pole | Outdoor
66kV Pole | Outdoor
33kV OHL (Tower Line) Conductor | Outdoor
33kV Tower | Outdoor
33kV Fittings | Outdoor
66kV OHL (Tower Line) Conductor | Outdoor
66kV Tower | Outdoor
66kV Fittings | Outdoor
33kV UG Cable (Non Pressurised) | n/a
33kV UG Cable (Oil) | n/a
33kV UG Cable (Gas) | n/a
66kV UG Cable (Non Pressurised) | n/a
66kV UG Cable (Oil) | n/a
66kV UG Cable (Gas) | n/a
EHV Sub Cable | n/a
33kV CB (Air Insulated Busbars)(ID) (GM) | Indoor
33kV CB (Air Insulated Busbars)(OD) (GM) | Outdoor
33kV CB (Gas Insulated Busbars)(ID)(GM) | Indoor
33kV CB (Gas Insulated Busbars)(OD)(GM) | Outdoor
33kV Switch (GM) | Indoor
33kV RMU | Indoor
66kV CB (Air Insulated Busbars)(ID) (GM) | Indoor
66kV CB (Air Insulated Busbars)(OD) (GM) | Outdoor
66kV CB (Gas Insulated Busbars)(ID)(GM) | Indoor
66kV CB (Gas Insulated Busbars)(OD)(GM) | Outdoor
33kV Transformer (GM) | Outdoor
Transformador 34kV (GM) | Outdoor
66kV Transformer (GM) | Outdoor
132kV OHL (Tower Line) Conductor | Outdoor
132kV Tower | Outdoor
132kV Fittings | Outdoor
132kV UG Cable (Non Pressurised) | n/a
132kV UG Cable (Oil) | n/a
132kV UG Cable (Gas) | n/a
132kV Sub Cable | n/a
132kV CB (Air Insulated Busbars)(ID) (GM) | Indoor
132kV CB (Air Insulated Busbars)(OD) (GM) | Outdoor
132kV CB (Gas Insulated Busbars)(ID) (GM) | Indoor
132kV CB (Gas Insulated Busbars)(OD) (GM) | Outdoor
132kV Transformer (GM) | Outdoor

## 27
Topography | Score (Sea) | Score (Land locked)
Low Detrimental Topography | 1.25 | 0.5
Medium Detrimental Topography | 1.5 | 0.6
High Detrimental Topography | 2.25 | 0.9
Very High Detrimental Topography | 3 | 1.2
Default | 1.25 | 0.5

## 28
Situation | Score
Laid on bed | 1
Covered | 0.9
Buried | 0.8
Default | 1

## 29
Rating | Description | Score
1 | Sheltered sea loch, Wind <200 W/m2 | 1
2 | Wave <15kW/m, Wind 200-800 W/m2 | 1.2
3 | Wave >15kW/m, Wind > 800 W/m2 | 1.4
| Default | 1

## 30
Intensity | Scoring (Sea) | Scoring (Landlocked)
Low | 1.1 | 1
Moderate | 1.25 | 1.15
High | 1.5 | 1.4
Default | 1.1 | 1

## 31A
Duty Factor 1 | Lower | Upper | Bound Description | Duty Factor (HV) | Duty Factor (EHV & 132kV)
DF1 | 0 | 50 | Maximum % Utilisation under normal operating conditions | 0.8 | 1
DF1 | 50 | 70 | Maximum % Utilisation under normal operating conditions | 0.9 | 1.1
DF1 | 70 | 100 | Maximum % Utilisation under normal operating conditions | 1 | 1.3
DF1 | 100 |  | Maximum % Utilisation under normal operating conditions | 1.8 | 2
DF1 | Default | Default | Maximum % Utilisation under normal operating conditions | 1 | 1

## 31B
Duty Factor 2 | Lower | Upper | Bound Description | Duty Factor
DF2 | 0 | 40 | Operating Voltage / Design Voltage (%) | 0.7
DF2 | 40 | 55 | Operating Voltage / Design Voltage (%) | 0.8
DF2 | 55 | 70 | Operating Voltage / Design Voltage (%) | 0.9
DF2 | 70 |  | Operating Voltage / Design Voltage (%) | 1
DF2 | Default | Default | Operating Voltage / Design Voltage (%) | 1

## 32
Number of operations | Duty Factor
Normal/Low | 1
High (eg: Auto-reclosers) | 1.2
Default | 1

## 33
Lower | Upper | Bound Description | Duty Factor
0 | 50 | Max % Utilisation under normal operating conditions | 0.9
50 | 70 | Max % Utilisation under normal operating conditions | 0.95
70 | 100 | Max % Utilisation under normal operating conditions | 1
100 |  | Max % Utilisation under normal operating conditions | 1.4
Default | Default | Max % Utilisation under normal operating conditions | 1

## 34
Lower | Upper | Bound Description | Duty Factor
0 | 50 | Max % Utilisation under normal operating conditions (Transformer) | 1
50 | 70 | Max % Utilisation under normal operating conditions (Transformer) | 1.05
70 | 100 | Max % Utilisation under normal operating conditions (Transformer) | 1.1
100 |  | Max % Utilisation under normal operating conditions (Transformer) | 1.4
Default | Default | Max % Utilisation under normal operating conditions (Transformer) | 1
0 | 7 | Average Number of Daily Taps (TapChanger) | 0.9
7 | 14 | Average Number of Daily Taps (TapChanger) | 1
14 | 28 | Average Number of Daily Taps (TapChanger) | 1.2
28 |  | Average Number of Daily Taps (TapChanger) | 1.3
Default | Default | Average Number of Daily Taps (TapChanger) | 1

## 35
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration | No observed deterioration | 0.9 | 10 | 0.5
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. Minor corrosion | 1.2 | 10 | 0.5
Substantial Deterioration | e.g. Major corrosion | 1.4 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 36
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
None | Dry | 1 | 10 | 0.5
Present in Pit | Evidence of moisture observed in pit | 1.1 | 10 | 0.5
Present in Bell Housing | Evidence of moisture observed in bell housing | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 37
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Satisfactory | No observed deterioration | 0.9 | 10 | 0.5
Some Deterioration | e.g. Minor corrosion | 1.2 | 10 | 0.5
Substantial Deterioration | e.g. Major corrosion | 1.4 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 38
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration | No observed deterioration | 0.9 | 10 | 0.5
Some Deterioration | Chips and advanced aging | 1 | 10 | 0.5
Substantial Deterioration | Evidence of flashover or damage, or degradation of insulation material | 1.3 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 39
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration | No observed deterioration | 0.9 | 10 | 0.5
Some Deterioration | Observed running higher than ambient | 1 | 10 | 0.5
Substantial Deterioration | Evidence of overheating | 1.5 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 40
Condition Criteria: Phase barriers Present? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Yes | Phase Barriers Present | 1 | 10 | 0.5
Missing | Phase Barriers Not Present (in whole or part) | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 41
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration: | Visual assessment gives a positive indication of asset condition. There are no obvious signs of any deterioration such as corrosion, stains or markings. | 0.9 | 10 | 0.5
Superficial/minor deterioration | There is little deterioration. The asset (or a sub component) may exhibit signs of ageing, surface level scratches, moss or lichen that can be brushed off. This has no material impact on the probability of failure for the asset. | 1 | 10 | 0.5
Some Deterioration | There is evidence of some degradation such as surface corrosion or minor compound leaks. The level of degradation may affect the operation of the asset if left untended (e.g. large patches of rust on the metalwork, doorhinges heavily rusted). | 1.3 | 10 | 0.5
Substantial Deterioration | The switchgear is corroded to the point that it can no longer hold its oil / SF6 insulation, one or more metalwork supports are rusted through, or the switchgear housing is damaged beyond economical repair | 1.6 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 42
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration: | Visual assessment gives a positive indication of asset condition. There are no obvious signs of any deterioration such as corrosion, stains or markings. | 0.9 | 10 | 0.5
Superficial/minor deterioration | There is little deterioration. The asset (or a sub component) may exhibit signs of ageing, surface level scratches, moss or lichen that can be brushed off. This has no material impact on the probability of failure for the asset | 1 | 10 | 0.5
Some Deterioration | There is evidence of some degradation such as surface corrosion or minor compound leaks. The level of degradation may affect the operation of the asset if left untended (e.g. large patches of rust on the metalwork, doorhinges heavily rusted). | 1.2 | 10 | 0.5
Substantial Deterioration | The switchgear is corroded to the point that one or more metalwork supports are rusted through, or the switchgear housing is damaged beyond economical repair | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 43
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration | No leakage | 1 | 10 | 0.5
Superficial/minor deterioration | Evidence of slight compound leak | 1.1 | 10 | 0.5
Substantial deterioration | Significant compound leak or multiple compound leaks on the same board. | 1.3 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 44
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration | No observed deterioration | 0.9 | 10 | 0.5
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | Minor corrosion (e.g. light rust) or evidence of a minor mechanism defect. | 1.2 | 10 | 3
Substantial Deterioration | Evidence of significant corrosion, missing, defective or damaged internal insulation (e.g. evidence of severe discharge activity or breakdown of insulation) or a severe mechanism defect that affects the operation of the asset | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 45
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Satisfactory | No observed deterioration | 0.9 | 10 | 0.5
Some Deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Substantial Deterioration | Degradation of insulation material | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 46
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration | No obvious degradation | 1 | 10 | 0.5
Minor Deterioration | Observed running higher than ambient | 1.2 | 10 | 0.5
Major Deterioration | Evidence of overheating | 1.5 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 47
Condition Criteria: Phase barriers Present? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Yes | Phase Barriers Present | 1 | 10 | 0.5
Missing | Phase Barriers Not Present (in whole or part) | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 48
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration: | Visual assessment gives a positive indication of asset condition. There are no obvious signs of any deterioration such as corrosion, stains or markings. | 0.9 | 10 | 0.5
Some DeterSuperficial/minor deteriorationioration | There is little deterioration The asset (or a sub component) may exhibit signs of ageing, surface level scratches, moss or lichen that can be brushed off. This has no material impact on the probability of failure for the asset. | 1 | 10 | 0.5
Some Deterioration | There is evidence of some degradation such as surface corrosion or minor compound leaks. The level of degradation may affect the operation of the asset if left untended (e.g. large patches of rust on the metalwork, doorhinges heavily rusted) | 1.2 | 10 | 0.5
Substantial Deterioration | The switchgear is corroded to the point that one or more metalwork supports are rusted through, or the switchgear housing is damaged beyond economical repair. | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 49
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration | No leakage | 1 | 10 | 0.5
Superficial/minor deterioration | Evidence of slight compound leak | 1.1 | 10 | 0.5
Substantial deterioration | Significant compound leak or multiple compound leaks on the same pillar. | 1.3 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 50
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration | No observed deterioration | 0.9 | 10 | 0.5
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | Minor corrosion (e.g. light rust) or evidence of a minor mechanism defect | 1.2 | 10 | 3
Substantial Deterioration | Evidence of significant corrosion, missing, defective or damaged internal insulation (e.g. evidence of severe discharge activity or breakdown of insulation) or a severe mechanism defect that affects the operation of the asset. | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 51
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Satisfactory | No observed deterioration | 0.9 | 10 | 0.5
Some Deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Substantial Deterioration | Degradation of insulation material | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 52
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration | No obvious degradation | 1 | 10 | 0.5
Minor Deterioration | Observed running higher than ambient | 1.2 | 10 | 0.5
Major Deterioration | Evidence of overheating | 1.5 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 53
Condition Criteria: Phase barriers Present? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Yes | Phase Barriers Present | 1 | 10 | 0.5
Missing | Phase Barriers Not Present (in whole or part) | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 54
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration: | Visual assessment gives a positive indication of asset condition. There are no obvious signs of any deterioration such as corrosion, stains or markings | 0.9 | 10 | 0.5
Superficial/minor deterioration | There is little deterioration. The asset (or a sub component) may exhibit signs of ageing, surface level scratches, moss or lichen that can be brushed off. This has no material impact on the probability of failure for the asset. | 1 | 10 | 0.5
Some Deterioration | There is evidence of some degradation such as surface corrosion or minor compound leaks. The level of degradation may affect the operation of the asset if left untended (e.g. large patches of rust on the metalwork, doorhinges heavily rusted). | 1.2 | 10 | 3
Substantial Deterioration | The switchgear is corroded to the point that it can no longer hold its oil / SF6 insulation, one or more metalwork supports are rusted through, or the switchgear housing is damaged beyond economical repair. | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 55
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration: | Oil: No Oil appears to be actively leaking from the component in question. This may include assets with minor stains or marks Gas: Gas pressure reading is within the expected limit | 0.9 | 10 | 0.5
Superficial/minor deterioration | Oil: There is evidence of a small leak, but this is limited to staining of the asset or the ground around the asset AND oil still visible in the sight glass where fitted. Repairs / intervention to the asset (or a sub component) is not expected to be required between now and the next planned maintenance Gas: Not used | 1 | 10 | 0.5
Some Deterioration | Oil: There is evidence of a small active oil leak from the switchgear e.g. droplets or weeping beneath the fixed portion. Minor maintenance or refurbishment activities (as a minimum) are required to address the identified issue(s) Gas: Gas pressure outside of acceptable range | 1.1 | 10 | 3
Substantial Deterioration | Oil: There is evidence of a significant oil leak from the switchgear e.g. pool of oil under/around the equipment, the switchgear may be draining or completely drained of oil and / or compound. Gas: Severe unrepairable leak or equipment requiring repeated top ups. | 1.3 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 56
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Ambient or Below | At or below ambient temperature | 0.9 | 10 | 0.5
Above Ambient | Above ambient temperature | 1 | 10 | 0.5
Substantially Above Ambient | Operating above the manufacturers recommended maximum temperature | 1.1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 57
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration: | No observed deterioration | 0.9 | 10 | 0.5
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | Minor corrosion (e.g. light rust) or evidence of a minor mechanism defect. | 1.2 | 10 | 3
Substantial Deterioration | Evidence of significant corrosion, missing, defective or damaged internal insulation (e.g. evidence of severe discharge activity or breakdown of insulation) or a severe mechanism defect that affects the operation of the asset | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 58
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Better than Expected | Air conditioned | 0.9 | 10 | 0.5
As Expected | This is an environment which is typified as dry and has a degree of background heating or dehumidification which maintains this year round. | 1 | 10 | 0.5
Deteriorated Environment | Heating or dehumidification faulty; room temperature is hotter than recommended by environmental policy; condensation evident in switch room etc. | 1.3 | 10 | 0.5
Severely Deteriorated Environment | The substation is showing major signs of dampness such as definite water marks around the building, significant amount of flaking paint and/or mould growth. No environmental controls (such as heating or dehumidification) are installed, or the installed environmental controls are not functioning adequately; room temperature is excessively hot; roof or structure permits water ingress; water stands in trenches or free water is observed in the switch room | 1.5 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 59
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration* | There are no signs of any deterioration such as corrosion, stains, markings, compound leaks, discharge etc | 1 | 10 | 0.5
Superficial / minor deterioration* | The cable box may exhibit minor exterior stains or marks (e.g. surface level scratches, moss or lichen that can be brushed off), but no damage or corrosion should be evident. No evidence of compound leaks, discharge, signs of heating, or deterioration of insulation. | 1 | 10 | 0.5
Some Deterioration | Minor corrosion (e.g. surface corrosion spots) or deterioration (e.g. minor breakthrough of paintwork but no loss of galvanising). | 1.1 | 10 | 0.5
Substantial Deterioration | Evidence of significant corrosion and perforation (e.g. holes). Severe breakthrough of paintwork with some loss of galvanising. Major compound leaks. Evidence of discharge, signs of heating, deterioration/ damage of insulation | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 60
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration: | Visual assessment gives a positive indication of asset condition. There are no obvious signs of any deterioration such as corrosion, stains or markings. | 0.9 | 10 | 0.5
Superficial / minor deterioration | There is little deterioration. The asset (or a sub component) may exhibit signs of ageing, surface level scratches, moss or lichen that can be brushed off. This has no material impact on the probability of failure for the asset | 1 | 10 | 0.5
Some Deterioration | There is evidence of some degradation such as surface corrosion or minor compound leaks. The level of degradation may affect the operation of the asset if left untended (e.g. large patches of rust on the metalwork, doorhinges heavily rusted) | 1.2 | 10 | 3
Substantial Deterioration | The switchgear is corroded to the point that it can no longer hold its oil / SF6 insulation, one or more metalwork supports are rusted through, or the switchgear housing is damaged beyond economical repair. | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 61
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration: | Oil: No Oil appears to be actively leaking from the component in question. This may include assets with minor stains or marks Gas: Gas pressure reading is within the expected limit | 0.9 | 10 | 0.5
Superficial / minor deterioration | Oil: There is evidence of a small leak, but this is limited to staining of the asset or the ground around the asset AND oil still visible in the sight glass where fitted. Repairs / intervention to the asset (or a sub component) is not expected to be required between now and the next planned maintenance Gas: Not used | 1 | 10 | 0.5
Some Deterioration | Oil: There is evidence of a small active oil leak from the switchgear e.g. droplets or weeping beneath the fixed portion. Minor maintenance or refurbishment activities (as a minimum) are required to address the identified issue(s) Gas: Gas pressure outside of acceptable range | 1.1 | 10 | 3
Substantial Deterioration | Oil: There is evidence of a significant oil leak from the switchgear e.g. pool of oil under/around the equipment, the switchgear may be draining or completely drained of oil and / or compound. Gas: Severe unrepairable leak or equipment requiring repeated top ups | 1.3 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 62
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Ambient or Below | At or below ambient temperature | 0.9 | 10 | 0.5
Above Ambient | Above ambient temperature | 1 | 10 | 0.5
Substantially Above Ambient | Operating above the manufacturers recommended maximum temperature | 1.1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 63
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration: | No observed deterioration | 0.9 | 10 | 0.5
Superficial / minor deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | Minor corrosion (e.g. light rust) or evidence of a minor mechanism defect. | 1.2 | 10 | 3
Substantial Deterioration | Evidence of significant corrosion, missing, defective or damaged internal insulation (e.g. evidence of severe discharge activity or breakdown of insulation) or a severe mechanism defect that affects the operation of the asset. | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 64
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Better than Expected | Air conditioned | 0.9 | 10 | 0.5
As Expected | This is an environment which is typified as dry and has a degree of background heating or dehumidification which maintains this year round. | 1 | 10 | 0.5
Deteriorated Environment | Heating or dehumidification faulty; room temperature is hotter than recommended by environmental policy; condensation evident in switch room etc. | 1.3 | 10 | 0.5
Severely Deteriorated Environment | The substation is showing major signs of dampness such as definite water marks around the building, significant amount of flaking paint and/or mould growth. No environmental controls (such as heating or dehumidification) are installed, or the installed environmental controls are not functioning adequately; room temperature is excessively hot; roof or structure permits water ingress; water stands in trenches or free water is observed in the switch room. | 1.5 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 65
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration* | There are no signs of any deterioration such as corrosion, stains, markings, compound leaks, discharge etc. | 1 | 10 | 0.5
Superficial / minor deterioration* | The cable box may exhibit minor exterior stains or marks (e.g. surface level scratches, moss or lichen that can be brushed off), but no damage or corrosion should be evident. No evidence of compound leaks, discharge, signs of heating, or deterioration of insulation. | 1 | 10 | 0.5
Some Deterioration | Minor corrosion (e.g. surface corrosion spots) or deterioration (e.g. minor breakthrough of paintwork but no loss of galvanising). | 1.1 | 10 | 0.5
Substantial Deterioration | Evidence of significant corrosion and perforation (e.g. holes). Severe breakthrough of paintwork with some loss of galvanising. Major compound leaks. Evidence of discharge, signs of heating, deterioration/ damage of insulation. | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 66
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration: | Visual assessment gives a positive indication of asset condition. There are no obvious signs of any deterioration such as corrosion, stains or markings | 0.9 | 10 | 0.5
Superficial / minor deterioration | There is little deterioration. The asset (or a sub component) may exhibit signs of ageing, surface level scratches, moss or lichen that can be brushed off. This has no material impact on the probability of failure for the asset. | 1 | 10 | 0.5
Some Deterioration | There is evidence of some degradation such as surface corrosion or minor compound leaks. The level of degradation may affect the operation of the asset if left untended (e.g. large patches of rust on the metalwork, doorhinges heavily rusted). | 1.2 | 10 | 3
Substantial Deterioration | The switchgear is corroded to the point that it can no longer hold its oil / SF6 insulation, one or more metalwork supports are rusted through, or the switchgear housing is damaged beyond economical repair. | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 67
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration: | Oil: No leakage, Gas: PressOil: No Oil appears to be actively leaking from the component in question. This may include assets with minor stains or marks Gas: Gas pressure reading is within the expected limiture within acceptable range | 0.9 | 10 | 0.5
Superficial / minor deterioration | Oil: There is evidence of a small leak, but this is limited to staining of the asset or the ground around the asset AND oil still visible in the sight glass where fitted. Repairs / intervention to the asset (or a sub component) is not expected to be required between now and the next planned maintenance Gas: Not used | 1 | 10 | 0.5
Some Deterioration | Oil: There is evidence of a small active oil leak from the switchgear e.g. droplets or weeping beneath the fixed portion. Minor maintenance or refurbishment activities (as a minimum) are required to address the identified issue(s) Gas: Gas pressure outside of acceptable range | 1.1 | 10 | 3
Substantial Deterioration | Oil: There is evidence of a significant oil leak from the switchgear e.g. pool of oil under/around the equipment, the switchgear may be draining or completely drained of oil and / or compound. Gas: Severe unrepairable leak or equipment requiring repeated top ups | 1.3 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 68
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Ambient or Below | At or below ambient temperature | 0.9 | 10 | 0.5
Above Ambient | Above ambient temperature | 1 | 10 | 0.5
Substantially Above Ambient | Operating above the manufacturers recommended maximum temperature | 1.1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 69
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration: | No observed deterioration | 0.9 | 10 | 0.5
Superficial / minor deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | Minor corrosion (e.g. light rust) or evidence of a minor mechanism defect. | 1.2 | 10 | 3
Substantial Deterioration | Evidence of significant corrosion, missing, defective or damaged internal insulation (e.g. evidence of severe discharge activity or breakdown of insulation) or a severe mechanism defect that affects the operation of the asset. | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 70
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Better than Expected | Air conditioned | 0.9 | 10 | 0.5
As Expected | This is an environment which is typified as dry and has a degree of background heating or dehumidification which maintains this year round. | 1 | 10 | 0.5
Deteriorated Environment | Heating or dehumidification faulty; room temperature is hotter than recommended by the environmental policy; condensation evident in switch room etc. | 1.3 | 10 | 0.5
Severely Deteriorated Environment | The substation is showing major signs of dampness such as definite water marks around the building, significant amount of flaking paint and/or mould growth. No environmental controls (such as heating or dehumidification) are installed, or the installed environmental controls are not functioning adequately; room temperature is excessively hot; roof or structure permits water ingress; water stands in trenches or free water is observed in the switch room | 1.5 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 71
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration: | Visual assessment gives a positive indication of asset condition. There are no obvious signs of any deterioration such as corrosion or cracks. | 0.9 | 10 | 0.5
Superficial / minor deterioration | Concrete Structures: Surface Deterioration Metal Structures: Minor localised surface corrosion | 1 | 10 | 0.5
Some Deterioration | Concrete Structures: Evidence of previous concrete repairs, repairs have begun to fail in places. This may include minor cracks and loss of section. Metal structures: some surface level corrosion. | 1.3 | 10 | 0.5
Substantial Deterioration | The support structure is corroded or damaged to the point that it can no longer fulfil its mechanical load carrying capacity. This may include: Concrete structures: extensive cracking, areas of concrete spalled exposing reinforcement causing corrosion. Metal structures: evidence of widespread or significant corrosion (e.g. perforation, holes in steelwork) or major physical damage. | 1.5 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 72
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration* | There are no signs of any deterioration such as corrosion, stains, markings, compound leaks, discharge etc | 1 | 10 | 0.5
Superficial / minor deterioration* | The cable box may exhibit minor exterior stains or marks (e.g. surface level scratches, moss or lichen that can be brushed off), but no damage or corrosion should be evident. No evidence of compound leaks, discharge, signs of heating, or deterioration of insulation | 1 | 10 | 0.5
Some Deterioration | Minor corrosion (e.g. surface corrosion spots) or deterioration (e.g. minor breakthrough of paintwork but no loss of galvanising). | 1.1 | 10 | 0.5
Substantial Deterioration | Evidence of significant corrosion and perforation (e.g. holes). Severe breakthrough of paintwork with some loss of galvanising. Major compound leaks. Evidence of discharge, signs of heating, deterioration/ damage of insulation | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 73
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration: | Visual assessment gives a positive indication of asset condition. There are no obvious signs of any deterioration such as corrosion, stains or markings. | 0.9 | 10 | 0.5
Superficial / minor deterioration | There is little deterioration. The asset (or a sub component) may exhibit signs of ageing, surface level scratches, moss or lichen that can be brushed off. This has no material impact on the probability of failure for the asset. | 1 | 10 | 0.5
Some Deterioration | There is evidence of some degradation such as surface corrosion or minor compound leaks. The level of degradation may affect the operation of the asset if left untended (e.g. large patches of rust on the metalwork, doorhinges heavily rusted). | 1.2 | 10 | 3
Substantial Deterioration | The switchgear is corroded to the point that it can no longer hold its oil / SF6 insulation, one or more metalwork supports are rusted through, or the switchgear housing is damaged beyond economical repair. | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 74
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration: | Oil: No Oil appears to be actively leaking from the component in question. This may include assets with minor stains or marks Gas: Gas pressure reading is within the expected limit | 0.9 | 10 | 0.5
Superficial / minor deterioration | Oil: There is evidence of a small leak, but this is limited to staining of the asset or the ground around the asset AND oil still visible in the sight glass where fitted. Repairs / intervention to the asset (or a sub component) is not expected to be required between now and the next planned maintenance Gas: Not used | 1 | 10 | 0.5
Some Deterioration | Oil: There is evidence of a small active oil leak from the switchgear e.g. droplets or weeping beneath the fixed portion. Minor maintenance or refurbishment activities (as a minimum) are required to address the identified issue(s) Gas: Gas pressure outside of acceptable range | 1.1 | 10 | 3
Substantial Deterioration | Oil: There is evidence of a significant oil leak from the switchgear e.g. pool of oil under/around the equipment, the switchgear may be draining or completely drained of oil and / or compound. Gas: Severe unrepairable leak or equipment requiring repeated top ups. | 1.3 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 75
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Ambient or Below | At or below ambient temperature | 0.9 | 10 | 0.5
Above Ambient | Above ambient temperature | 1 | 10 | 0.5
Substantially Above Ambient | Operating above the manufacturers recommended maximum temperature | 1.1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 76
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration: | No observed deterioration | 0.9 | 10 | 0.5
Superficial / minor deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | Minor corrosion (e.g. light rust) or evidence of a minor mechanism defect. | 1.2 | 10 | 3
Substantial Deterioration | Evidence of significant corrosion, missing, defective or damaged internal insulation (e.g. evidence of severe discharge activity or breakdown of insulation) or a severe mechanism defect that affects the operation of the asset. | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 77
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Better than Expected | Air conditioned | 0.9 | 10 | 0.5
As Expected | This is an environment which is typified as dry and has a degree of background heating or dehumidification which maintains this year round. | 1 | 10 | 0.5
Deteriorated Environment | Heating or dehumidification faulty; room temperature is hotter than recommended by environmental policy; condensation evident in switch room etc | 1.3 | 10 | 0.5
Severely Deteriorated Environment | The substation is showing major signs of dampness such as definite water marks around the building, significant amount of flaking paint and/or mould growth. No environmental controls (such as heating or dehumidification) are installed, or the installed environmental controls are not functioning adequately; room temperature is excessively hot; roof or structure permits water ingress; water stands in trenches or free water is observed in the switch room | 1.5 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 78
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration: | Visual assessment gives a positive indication of asset condition. There are no obvious signs of any deterioration such as corrosion or cracks. | 0.9 | 10 | 0.5
Superficial / minor deterioration | Concrete Structures: Surface Deterioration Metal Structures: Minor localised surface corrosion | 1 | 10 | 0.5
Some Deterioration | Concrete Structures: Evidence of previous concrete repairs, repairs have begun to fail in places. This may include minor cracks and loss of section. Metal structures: some surface level corrosion. | 1.3 | 10 | 0.5
Substantial Deterioration | The support structure is corroded or damaged to the point that it can no longer fulfil its mechanical load carrying capacity. This may include: Concrete structures: extensive cracking, areas of concrete spalled exposing reinforcement causing corrosion. Metal structures: evidence of widespread or significant corrosion (e.g. perforation, holes in steelwork) or major physical damage | 1.5 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 79
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration: | No observed deterioration | 0.9 | 10 | 0.5
Superficial / minor deterioration | Minor surface corrosion observed on observable pipe work | 1 | 10 | 0.5
Some Deterioration | Minor Air Losses - System runs excessively to maintain pressure | 1.3 | 10 | 0.5
Substantial Deterioration | Major Air Losses - Loss of pressure pipe section observed. Air leaks can be found by inspection; Certification notes defects. Etc. | 1.5 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 80
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration* | There are no signs of any deterioration such as corrosion, stains, markings, compound leaks, discharge etc. | 1 | 10 | 0.5
Superficial / minor deterioration* | The cable box may exhibit minor exterior stains or marks (e.g. surface level scratches, moss or lichen that can be brushed off), but no damage or corrosion should be evident. No evidence of compound leaks, discharge, signs of heating, or deterioration of insulation | 1 | 10 | 0.5
Some Deterioration | Minor corrosion (e.g. surface corrosion spots) or deterioration (e.g. minor breakthrough of paintwork but no loss of galvanising). | 1.1 | 10 | 0.5
Substantial Deterioration | Evidence of significant corrosion and perforation (e.g. holes). Severe breakthrough of paintwork with some loss of galvanising. Major compound leaks. Evidence of discharge, signs of heating, deterioration/ damage of insulation. | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 81
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration | Condition as new | 0.9 | 10 | 0.5
Superficial/minor deterioration | The transformer may exhibit signs of ageing or marks (e.g. surface level scratches, moss or lichen that can be brushed off). This has no material impact on the probability of failure for the asset. | 1 | 10 | 0.5
Slight deterioration | Minor localised surface corrosion. There may be evidence of a small leak, but it does not present a significant impact to the overall probability of failure for the asset, for example: - There is a small active leak from a sub component but this can be addressed through intervention of the sub component - A small inactive leak which is limited to staining of the asset or the ground around the asset. | 1.1 | 10 | 0.5
Some Deterioration | The asset shows a level of deterioration such as surface corrosion spots. The level of degradation may affect the operation of the asset if left untended (e.g. large patches of rust on the metalwork); and/or there is evidence of a small active oil leak (e.g. droplets or weeping). | 1.25 | 10 | 3
Substantial Deterioration | There is evidence of major corrosion or a significant active oil leak (e.g. pools of oil collecting on the ground or plinth). | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 82
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration* | There are no signs of any deterioration such as corrosion, stains, markings, compound leaks, discharge etc. | 1 | 10 | 0.5
Superficial / minor deterioration* | The cable box may exhibit minor exterior stains or marks (e.g. surface level scratches, moss or lichen that can be brushed off), but no damage or corrosion should be evident. No evidence of compound leaks, discharge, signs of heating, or deterioration of insulation | 1 | 10 | 0.5
Some Deterioration | Minor corrosion (e.g. surface corrosion spots) or deterioration (e.g. minor breakthrough of paintwork but no loss of galvanising). | 1.1 | 10 | 0.5
Substantial Deterioration | Evidence of significant corrosion and perforation (e.g. holes). Severe breakthrough of paintwork with some loss of galvanising. Major compound leaks. Evidence of discharge, signs of heating, deterioration/ damage of insulation | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 83
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Superficial/minor deterioration | The transformer may exhibit signs of ageing or marks (e.g. surface level scratches, moss or lichen that can be brushed off). This has no material impact on the probability of failure for the asset. There may be evidence of a small leak, but it does not present a significant impact to the overall probability of failure for the asset, for example: - There is a small active leak from a sub component (e.g. a pressure relief device) but this can be addressed through intervention of the sub component. - The leak this is limited to staining of the asset or the ground around the asset. | 1 | 10 | 0.5
Some Deterioration | The asset shows a level of deterioration such as surface corrosion spots or minor oil leaks. The level of degradation may affect the operation of the asset if left untended (e.g. large patches of rust on the metalwork); and/or there is evidence of a small active oil leak (e.g. droplets or weeping). | 1.4 | 10 | 4
Substantial Deterioration | There is evidence of major corrosion or a significant active and unrepairable oil leak (e.g. pools of oil collecting on the ground or plinth). | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 84
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Superficial/minor deterioration | The asset (or a sub component) may exhibit signs of ageing, minor stains or marks (e.g. surface level scratches, moss or lichen that can be brushed off). This has no material impact on the probability of failure for the asset. | 1 | 10 | 0.5
Some Deterioration | Localised areas of surface corrosion or evidence of oil leaks not associated with the transformer fins (e.g. manifolds and associated pipework, flanges, couplings, valves) | 1.2 | 10 | 0.5
Substantial Deterioration | Widespread corrosion, loss of crosssectional area or thinning or evidence of oil leakage from the fins. | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 85
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | Minor corrosion or evidence of a historic oil leak (e.g. stains) or minor damage (e.g. small chips or cracks). Bushings with high levels of pollution with associated evidence of localised discharge or tracking | 1.2 | 10 | 0.5
Substantial Deterioration | Visible cracks, broken sheds, damage, surface degradation, widespread/significant discharge activity and/or active oil leak (e.g. droplets, pools of oil). | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 86
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Superficial/minor deterioration | The asset component exhibits some deterioration but is fit for continued service. There is no or little obvious signs of corrosion | 1 | 10 | 0.5
Some Deterioration | The component asset shows a level of deterioration such as surface corrosion spots. The level of degradation may affect the operation of the asset if left untended (e.g. large patches of rust on the metalwork). | 1.1 | 10 | 0.5
Substantial Deterioration | There is evidence of major corrosion or damage affecting the structural integrity | 1.2 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 87
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration* | There are no signs of any deterioration such as corrosion, stains, markings, compound leaks, discharge etc. | 1 | 10 | 0.5
Superficial / minor deterioration* | The cable box may exhibit minor exterior stains or marks (e.g. surface level scratches, moss or lichen that can be brushed off), but no damage or corrosion should be evident. No evidence of compound leaks, discharge, signs of heating, or deterioration of insulation | 1 | 10 | 0.5
Some Deterioration | Minor corrosion (e.g. surface corrosion spots) or deterioration (e.g. minor breakthrough of paintwork but no loss of galvanising). | 1.1 | 10 | 0.5
Substantial Deterioration | Evidence of significant corrosion and perforation (e.g. holes). Severe breakthrough of paintwork with some loss of galvanising. Major compound leaks. Evidence of discharge, signs of heating, deterioration/ damage of insulation | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 88
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. Minor corrosion or evidence of compound leaks (where appropriate) | 1.4 | 10 | 4
Substantial Deterioration | e.g. Major corrosion or evidence of low level oil leaks (If appropriate) | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 89
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or evidence of low level oil leaks (If appropriate) | 1.2 | 10 | 3
Substantial Deterioration | e.g. observed or potential mechanism defect, internal insulation, etc. | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 90
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration: | No observed deterioration | 0.9 | 10 | 0.5
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or wear to components | 1.2 | 10 | 0.5
Substantial Deterioration | e.g. major corrosion or excessive wear in component and bearings | 1.4 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 91
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration: | No observed deterioration | 0.95 | 10 | 0.5
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or wear to components | 1.1 | 10 | 0.5
Substantial Deterioration | e.g. major corrosion or excessive wear in component and bearings | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 92
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration: | No observed deterioration | 0.95 | 10 | 0.5
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or wear | 1.05 | 10 | 0.5
Substantial Deterioration | e.g. major corrosion or fraying of braids | 1.1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 93
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Superficial/minor deterioration | The transformer may exhibit signs of ageing or marks (e.g. surface level scratches, moss or lichen that can be brushed off). This has no material impact on the probability of failure for the asset. There may be evidence of a small leak, but it does not present a significant impact to the overall probability of failure for the asset, for example: - There is a small active leak from a sub component (e.g. a pressure relief device) but this can be addressed through intervention of the sub component. The leak this is limited to staining of the asset or the ground around the asset | 1 | 10 | 0.5
Some Deterioration | The asset shows a level of deterioration such as surface corrosion spots or minor oil leaks. The level of degradation may affect the operation of the asset if left untended (e.g. large patches of rust on the metalwork); and/or there is evidence of a small active oil leak (e.g. droplets or weeping). | 1.4 | 10 | 4
Substantial Deterioration | There is evidence of major corrosion or a significant active and unrepairable oil leak (e.g. pools of oil collecting on the ground or plinth). | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 94
Condition Criteria | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Superficial/minor deterioration | The asset (or a sub component) may exhibit signs of ageing, minor stains or marks (e.g. surface level scratches, moss or lichen that can be brushed off). This has no material impact on the probability of failure for the asset. | 1 | 10 | 0.5
Some Deterioration | Localised areas of surface corrosion or evidence of oil leaks not associated with the transformer fins (e.g. manifolds and associated pipework, flanges, couplings, valves) | 1.2 | 10 | 0.5
Substantial Deterioration | Widespread corrosion, loss of crosssectional area or thinning or evidence of oil leakage from the fins. | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 95
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | Minor corrosion or evidence of a historic oil leak (e.g. stains) or minor damage (e.g. small chips or cracks). Bushings with high levels of pollution with associated evidence of localised discharge or tracking. | 1.2 | 10 | 0.5
Substantial Deterioration | Visible cracks, broken sheds, damage, surface degradation, widespread/significant discharge activity and/or active oil leak (e.g. droplets, pools of oil). | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 96
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Superficial/minor deterioration | The asset component exhibits some deterioration but is fit for continued service. There is no or little obvious signs of corrosion. | 1 | 10 | 0.5
Some Deterioration | The component asset shows a level of deterioration such as surface corrosion spots. The level of degradation may affect the operation of the asset if left untended (e.g. large patches of rust on the metalwork). | 1.1 | 10 | 0.5
Substantial Deterioration | There is evidence of major corrosion or damage affecting the structural integrity. | 1.2 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 97
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No Deterioration* | There are no signs of any deterioration such as corrosion, stains, markings, compound leaks, discharge etc. | 1 | 10 | 0.5
Superficial / minor deterioration* | The cable box may exhibit minor exterior stains or marks (e.g. surface level scratches, moss or lichen that can be brushed off), but no damage or corrosion should be evident. No evidence of compound leaks, discharge, signs of heating, or deterioration of insulation | 1 | 10 | 0.5
Some Deterioration | Minor corrosion (e.g. surface corrosion spots) or deterioration (e.g. minor breakthrough of paintwork but no loss of galvanising). | 1.1 | 10 | 0.5
Substantial Deterioration | Evidence of significant corrosion and perforation (e.g. holes). Severe breakthrough of paintwork with some loss of galvanising. Major compound leaks. Evidence of discharge, signs of heating, deterioration/ damage of insulation | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 98
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or evidence of low level oil leaks (If appropriate) | 1.4 | 10 | 4
Substantial Deterioration | e.g. major corrosion or evidence of significant oil leakage | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 99
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or evidence of low level oil leaks (If appropriate) | 1.2 | 10 | 3
Substantial Deterioration | e.g. observed or potential mechanism defect, internal insulation, etc+ | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 100
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration | No observed deterioration | 0.9 | 10 | 0.5
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or wear to components | 1.2 | 10 | 0.5
Substantial Deterioration | e.g. major corrosion or excessive wear in component and bearings | 1.4 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 101
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration | No observed deterioration | 0.95 | 10 | 0.5
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or wear | 1.1 | 10 | 0.5
Substantial Deterioration | e.g. major corrosion or excessive wear in component and bearings | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 102
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration | No observed deterioration | 0.95 | 10 | 0.5
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion or wear | 1.05 | 10 | 0.5
Substantial Deterioration | e.g. major corrosion or fraying of braids | 1.1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 103
Condition Criteria: Lead Crystallisation Present? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No | Applicable to cables in the Lead sheath sub-division only: No lead crystallisation has been identified in the sheath of the cable or any other lead sheath cable within the same hydraulic section, on any occasion where the lead sheath of the cable has been exposed (e.g. during fault repair, leak location, construction works etc.). | 1 | 10 | 0.5
Yes | Applicable to cables in the Lead sheath sub-division only: Evidence of lead crystallisation has been identified in the sheath of the cable or any other lead sheath cable within the same hydraulic section, on one or more occasions where the lead sheath of the cable has been exposed (e.g. during fault repair, leak location, construction works etc.). | 1.8 | 10 | 8
Not applicable | This condition input is not applicable because the exposed cable within the hydraulic section is in the Aluminium sheath sub-division or the Lead sheath cable section has not been exposed. | 1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 104
Condition Criteria: Lead Crystallisation Present? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No | Applicable to cables in the Lead sheath sub-division only: No lead crystallisation has been identified in the sheath of the cable or any other lead sheath cable within the same hydraulic section, on any occasion where the lead sheath of the cable has been exposed (e.g. during fault repair, leak location, construction works etc.). | 1 | 10 | 0.5
Yes | Applicable to cables in the Lead sheath sub-division only: Evidence of lead crystallisation has been identified in the sheath of the cable or any other lead sheath cable within the same hydraulic section, on one or more occasions where the lead sheath of the cable has been exposed (e.g. during fault repair, leak location, construction works etc.). | 1.8 | 10 | 8
Not applicable | This condition input is not applicable because the exposed cable within the hydraulic section is in the Aluminium sheath sub-division or the Lead sheath cable section has not been exposed. | 1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 105
Condition Criteria: Lead Crystallisation Present? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No | Applicable to cables in the Lead sheath sub-division only: No lead crystallisation has been identified in the sheath of the cable or any other lead sheath cable within the same hydraulic section, on any occasion where the lead sheath of the cable has been exposed (e.g. during fault repair, leak location, construction works etc.). | 1 | 10 | 0.5
Yes | Applicable to cables in the Lead sheath sub-division only: Evidence of lead crystallisation has been identified in the sheath of the cable or any other lead sheath cable within the same hydraulic section, on one or more occasions where the lead sheath of the cable has been exposed (e.g. during fault repair, leak location, construction works etc.). | 1.8 | 10 | 8
Not applicable | This condition input is not applicable because the exposed cable within the hydraulic section is in the Aluminium sheath sub-division or the Lead sheath cable section has not been exposed. | 1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 106
Condition Criteria: Lead Crystallisation Present? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No | Applicable to cables in the Lead sheath sub-division only: No lead crystallisation has been identified in the sheath of the cable or any other lead sheath cable within the same hydraulic section, on any occasion where the lead sheath of the cable has been exposed (e.g. during fault repair, leak location, construction works etc.). | 1 | 10 | 0.5
Yes | Applicable to cables in the Lead sheath sub-division only: Evidence of lead crystallisation has been identified in the sheath of the cable or any other lead sheath cable within the same hydraulic section, on one or more occasions where the lead sheath of the cable has been exposed (e.g. during fault repair, leak location, construction works etc.). | 1.8 | 10 | 8
Not applicable | This condition input is not applicable because the exposed cable within the hydraulic section is in the Aluminium sheath sub-division or the Lead sheath cable section has not been exposed. | 1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 107
Condition Criteria | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Good | The asset component exhibits deterioration but is fit for continued service | 1 | 10 | 0.5
Poor | e.g. visible damage to armour | 1.6 | 10 | 5.5
Critical | e.g. mechanical damage to cable armour, loss of armour | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 108
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable | No significant defects observed. Pole may be new with no/few marks. May include poles with slight damage including (but not limited to) splits and general wear where no material impact on residual strength of pole. | 1 | 10 | 0.5
Some Deterioration | Minor wear on pole or physical damage that will lead to loss of strength, but the short term integrity of the pole is not compromised. | 1.3 | 10 | 4
Substantial Deterioration | Severe damage to pole. Parts may be chipped off, rotten or disfigured. e.g. visible splits, cracks, major physical damage affecting strength. | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 109
Condition Criteria: Pole Top Rot Present? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No | No pole top rot observed | 1 | 10 | 0.5
Yes | Pole top rot is observed | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 110
Condition Criteria: Pole Leaning? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No | The pole is vertical | 1 | 10 | 0.5
Yes | The pole is not vertical | 1.2 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 111
Condition Criteria: Bird/ Animal Damage? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No | There is no animal damage | 1 | 10 | 0.5
Yes | There is animal damage | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 112
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable | No significant defects observed. Pole may be new with no/few marks. May include poles with slight damage including (but not limited to) splits and general wear where no material impact on residual strength of pole. | 1 | 10 | 0.5
Some Deterioration | Minor wear on pole or physical damage that will lead to loss of strength, but the short term integrity of the pole is not compromised. | 1.3 | 10 | 4
Substantial Deterioration | Severe damage to pole. Parts may be chipped off, rotten or disfigured. E.g. visible splits, cracks, major physical damage affecting strength. | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 113
Condition Criteria: Pole Top Rot Present? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No | No pole top rot observed | 1 | 10 | 0.5
Yes | Pole top rot is observed | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 114
Condition Criteria: Pole Leaning? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No | The pole is vertical | 1 | 10 | 0.5
Yes | The pole is not vertical | 1.2 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 115
Condition Criteria: Bird/ Animal Damage? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No | There is no animal damage | 1 | 10 | 0.5
Yes | There is animal damage | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 116
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable | No significant defects observed. Pole may be new with no/few marks. May include poles with slight damage including (but not limited to) splits and general wear where no material impact on residual strength of pole. | 1 | 10 | 0.5
Some Deterioration | Minor wear on pole or physical damage that will lead to loss of strength, but the short term integrity of the pole is not compromised. | 1.3 | 10 | 4
Substantial Deterioration | Severe damage to pole. Parts may be chipped off, rotten or disfigured. E.g. visible splits, cracks, major physical damage affecting strength. | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 117
Condition Criteria: Pole Top Rot Present? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No | No pole top rot observed | 1 | 10 | 0.5
Yes | Pole top rot is observed | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 118
Condition Criteria: Pole Leaning? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No | The pole is vertical | 1 | 10 | 0.5
Yes | The pole is not vertical | 1.2 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 119
Condition Criteria: Bird/ Animal Damage? | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No | There is no animal damage | 1 | 10 | 0.5
Yes | There is animal damage | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 120
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable |  | 1 | 4.4 | 0.5
Mechanically Unsafe | Signs of wasting of steel cross-section, laminated rust, holes or loss of steel at edges, severe damage - requires urgent replacement | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 121
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable |  | 1 | 4.4 | 0.5
Mechanically Unsafe | Signs of wasting of steel cross-section, laminated rust, holes or loss of steel at edges, severe damage - requires urgent replacement | 1.2 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 122
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable |  | 1 | 4.4 | 0.5
Mechanically Unsafe | Signs of wasting of steel cross-section, laminated rust, holes or loss of steel at edges, severe damage - requires urgent replacement | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 123
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable |  | 1 | 4.4 | 0.5
Mechanically Unsafe | Signs of wasting of steel cross-section, laminated rust, holes or loss of steel at edges, severe damage - requires urgent replacement | 1.2 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 124
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration |  | 1 | 6.4 | 0.5
Superficial/minor deterioration | Slight rust breakthrough - up to 5% of surface area affected. | 1.1 | 6.4 | 0.5
Some Deterioration | Moderate rust breakthrough - between 5% and 20% of surface area affected, and/or pitted rust | 1.6 | 6.4 | 0.5
Substantial Deterioration | Severe rust breakthrough - more than 20% of surface area affected, AND/OR damaged or bent steelwork, AND/OR any blistered paintwork with evidence of severe rust underneath, painting/attention required urgently | 1.8 | 6.4 | 5.5
Default | No data available | 1 | 6.4 | 0.5

## 125
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration | No observed deterioration | 0.95 | 4.4 | 0.5
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 4.4 | 0.5
Some Deterioration | e.g. minor corrosion | 1.4 | 10 | 4
Substantial Deterioration | n Insufficient integrity to support tower loading | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 126
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable |  | 1 | 4.4 | 0.5
Mechanically Unsafe | Signs of wasting of steel cross-section, laminated rust, holes or loss of steel at edges, severe damage - requires urgent replacement | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 127
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable |  | 1 | 4.4 | 0.5
Mechanically Unsafe | Signs of wasting of steel cross-section, laminated rust, holes or loss of steel at edges, severe damage - requires urgent replacement | 1.2 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 128
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable |  | 1 | 4.4 | 0.5
Mechanically Unsafe | Signs of wasting of steel cross-section, laminated rust, holes or loss of steel at edges, severe damage - requires urgent replacement | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 129
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable |  | 1 | 4.4 | 0.5
Mechanically Unsafe | Signs of wasting of steel cross-section, laminated rust, holes or loss of steel at edges, severe damage - requires urgent replacement | 1.2 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 130
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration |  | 1 | 6.4 | 0.5
Superficial/minor deterioration | Slight rust breakthrough - up to 5% of surface area affected. | 1.1 | 6.4 | 0.5
Some Deterioration | Moderate rust breakthrough - between 5% and 20% of surface area affected, and/or pitted rust | 1.6 | 6.4 | 0.5
Substantial Deterioration | Severe rust breakthrough - more than 20% of surface area affected, AND/OR damaged or bent steelwork, AND/OR any blistered paintwork with evidence of severe rust underneath, painting/attention required urgently. | 1.8 | 6.4 | 5.5
Default | No data available | 1 | 6.4 | 0.5

## 131
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration | No observed deterioration | 0.95 | 4.4 | 0.5
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1 | 4.4 | 0.5
Some Deterioration | e.g. minor corrosion | 1.4 | 10 | 4
Substantial Deterioration | Insufficient integrity to support tower loading | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 132
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration | No observed deterioration | 0.9 | 10 | 0.5
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1.1 | 10 | 0.5
Some Deterioration | Partial Loss of required structural integrity | 1.3 | 10 | 4
Substantial Deterioration | Loss of required structural integrity | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 133
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration | No observed deterioration | 0.9 | 10 | 0.5
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1.1 | 10 | 0.5
Some Deterioration | Partial Loss of required structural integrity | 1.3 | 10 | 4
Substantial Deterioration | Loss of required structural integrity | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 134
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration | No observed deterioration | 0.9 | 10 | 0.5
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1.1 | 10 | 0.5
Some Deterioration | Partial Loss of required structural integrity | 1.3 | 10 | 4
Substantial Deterioration | Loss of required structural integrity | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 135
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration | No observed deterioration | 0.9 | 10 | 0.5
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1.1 | 10 | 0.5
Some Deterioration | Partial Loss of required structural integrity | 1.3 | 10 | 4
Substantial Deterioration | Loss of required structural integrity | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 136
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration | No observed deterioration | 0.9 | 10 | 0.5
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1.1 | 10 | 0.5
Some Deterioration | Partial Loss of required structural integrity | 1.3 | 10 | 4
Substantial Deterioration | Loss of required structural integrity | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 137
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration | No observed deterioration | 0.9 | 10 | 0.5
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1.1 | 10 | 0.5
Some Deterioration | Partial Loss of required structural integrity | 1.3 | 10 | 4
Substantial Deterioration | Loss of required structural integrity | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 138
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration | No observed deterioration | 0.9 | 10 | 0.5
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1.1 | 10 | 0.5
Some Deterioration | Partial Loss of required structural integrity | 1.3 | 10 | 4
Substantial Deterioration | Loss of required structural integrity | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 139
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration | No observed deterioration | 0.9 | 10 | 0.5
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1.1 | 10 | 0.5
Some Deterioration | Partial Loss of required structural integrity | 1.3 | 10 | 4
Substantial Deterioration | Loss of required structural integrity | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 140
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration | No observed deterioration | 0.9 | 10 | 0.5
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1.1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion | 1.3 | 10 | 4
Substantial Deterioration | e.g. bird caging, broken strands, loss of section | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 141
Condition Criteria: No. of Midspan Joints | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
0 | No joints in the span. A span includes all conductors in that span | 1 | 10 | 0.5
1 | 1 joint in the span | 1.05 | 10 | 0.5
2 | 2 joints in the span | 1.1 | 10 | 0.5
>2 | More than two joints in the span | 1.2 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 142
Condition Criteria: Observed Condition | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No deterioration | No observed deterioration | 0.9 | 10 | 0.5
Superficial/minor deterioration | The asset component is fit for continued service. There is little deterioration | 1.1 | 10 | 0.5
Some Deterioration | e.g. minor corrosion | 1.3 | 10 | 4
Substantial Deterioration | e.g. bird caging, broken strands, loss of section | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 143
Condition Criteria: No. of Midspan Joints | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
0 | No joints in the span. A span includes all conductors in that span | 1 | 10 | 0.5
1 | 1 joint in the span | 1.05 | 10 | 0.5
2 | 2 joints in the span | 1.1 | 10 | 0.5
>2 | More than two joints in the span | 1.2 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 144
Condition Criteria: Operational Adequacy | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Operable | The LV UGB can be operated safely | 1 | 10 | 0.5
Inoperable | The LV UGB cannot be operated or repaired | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 145
Condition Criteria: Operational Adequacy | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Acceptable | The device can be operated safely | 1 | 10 | 0.5
Unacceptable | The device cannot be operated safely | 1.6 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 146
Condition Criteria: Operational Adequacy | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Operable | The LV Board can be operated safely | 1 | 10 | 0.5
Inoperable - Secure | The LV Board cannot be operated but is physically secure | 1.3 | 10 | 4
Inoperable - Hazardous | The LV Board cannot be operated and presents a hazard to either operator, the public or both | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 147
Condition Criteria: Operational Adequacy | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Operable | The LV Board can be operated safely | 1 | 10 | 0.5
Inoperable - Secure | The LV Board cannot be operated but is physically secure | 1.3 | 10 | 4
Inoperable - Hazardous | The LV Board cannot be operated and presents a hazard to either operator, the public or both | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 148
Condition Criteria: Partial Discharge Test Results | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | Low or negligible levels of partial discharge indicating no issues identified (e.g. a green condition using a TEV or <10% of manufacturers recommendation | 1 | 10 | 0.5
Medium | Some moderate levels of partial discharge recorded (e.g. ‘Amber’ result from TEV measuring device or between 10% and 30% of the manufacturers recommendation) | 1.1 | 10 | 0.5
High (Not Confirmed) | High levels of partial discharge indicating possible defect with plant / equipment, requiring further investigation (e.g. ‘Red’ result from TEV measuring device or above manufacturers recommendation) | 1.3 | 10 | 5.5
High (Confirmed) | High partial discharge. Source of partial discharge confirmed as potential source of failure | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 149
Lower | Upper | Bound Description | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | As New | Condition Criteria: Ductor Test Results in % | The joint test result meets the manufacturers recommended value | 1 | 10 | 0.5
0 | 10 | Condition Criteria: Ductor Test Results, Deterioration from new in % | Up to 10% deterioration from the ‘As New’ condition | 1.1 | 10 | 0.5
10 |  | Condition Criteria: Ductor Test Results, Deterioration from new in % | Over 10% deterioration from the ‘As New’ condition | 1.3 | 10 | 0.5
Default | Default | Condition Criteria: Ductor Test Results | No data available | 1 | 10 | 0.5

## 150
Lower | Upper | Bound Description | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | As New | Condition Criteria: Oil Test Results in % | The joint test result meets the manufacturers recommended value | 1 | 10 | 0.5
0 | 10 | Condition Criteria: Oil Test Results, Deterioration from new in % | Up to 10% deterioration from the ‘As New’ condition | 1.1 | 10 | 0.5
10 |  | Condition Criteria: Oil Test Results, Deterioration from new in % | Over 10% deterioration from the ‘As New’ condition | 1.3 | 10 | 0.5
Default | Default | Condition Criteria: Oil Test Results | No data available | 1 | 10 | 0.5

## 151
Condition Criteria: Temperature Readings | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Ambient or Below | At or below ambient temperature | 0.9 | 10 | 0.5
Above Ambient | Above ambient temperature | 1 | 10 | 0.5
Substantially Above Ambient | Operating above the manufacturers recommended maximum temperature | 1.1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 152
Condition Criteria: Trip Timing Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Pass | Trip time within acceptable range for the type of switchgear | 1 | 10 | 0.5
Fail | Trip time slower than acceptable time for the type of switchgear | 1.4 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 153
Condition Criteria: Partial Discharge Test Results | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | Low or negligible levels of partial discharge indicating no issues identified (e.g. a green condition using a TEV or <10% of manufacturers recommendation | 1 | 10 | 0.5
Medium | Some moderate levels of partial discharge recorded (e.g. ‘Amber’ result from TEV measuring device or between 10% and 30% of the manufacturers recommendation) | 1.1 | 10 | 0.5
High (Not Confirmed) | High levels of partial discharge indicating possible defect with plant / equipment, requiring further investigation (e.g. ‘Red’ result from TEV measuring device or above manufacturers recommendation) | 1.3 | 10 | 5.5
High (Confirmed) | High partial discharge. Source of partial discharge confirmed as potential source of failure | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 154
Condition Criteria: Ductor Test Results | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | The joint test result meets the manufacturers recommended value | 1 | 10 | 0.5
Upto 10% deterioration from New | Up to 10% deterioration from the ‘As New’ condition | 1.1 | 10 | 0.5
> 10% deterioration from New | Over 10% deterioration from the ‘As New’ condition | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 155
Condition Criteria: IR Test Results | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | The insulation test result meets the manufacturers recommended value | 1 | 10 | 0.5
Upto 10% deterioration from New | Up to 10% deterioration from the ‘As New’ condition | 1.1 | 10 | 0.5
> 10% deterioration from New | Over 10% deterioration from the ‘As New’ condition | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 156
Condition Criteria: Oil Test Results | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | The oil test result meets the required European Standard for new oil or gas | 1 | 10 | 0.5
Upto 10% deterioration from New | Up to 10% deterioration from the ‘As New’ condition | 1.1 | 10 | 0.5
> 10% deterioration from New | Over 10% deterioration from the ‘As New’ condition | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 157
Condition Criteria: Temperature Readings | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Ambient or Below | At or below ambient temperature | 0.9 | 10 | 0.5
Above Ambient | Above ambient temperature | 1 | 10 | 0.5
Substantially Above Ambient | Operating above the manufacturers recommended maximum temperature | 1.1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 158
Condition Criteria: Trip Timing Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Pass | Trip time within acceptable range for the type of switchgear | 1 | 10 | 0.5
Fail | Trip time slower than acceptable time for the type of switchgear | 1.4 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 159
Condition Criteria: Partial Discharge Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | Low or negligible levels of partial discharge indicating no issues identified (e.g. a green condition using a TEV or <10% of manufacturers recommendation | 1 | 10 | 0.5
Medium | Some moderate levels of partial discharge recorded (e.g. ‘Amber’ result from TEV measuring device or between 10% and 30% of the manufacturers recommendation) | 1.1 | 10 | 0.5
High (Not Confirmed) | High levels of partial discharge indicating possible defect with plant / equipment, requiring further investigation (e.g. ‘Red’ result from TEV measuring device or above manufacturers recommendation) | 1.3 | 10 | 5.5
High (Confirmed) | High partial discharge. Source of partial discharge confirmed as potential source of failure | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 160
Condition Criteria: Ductor Test Results | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | The joint test result meets the manufacturers recommended value | 1 | 10 | 0.5
Upto 10% deterioration from New | Up to 10% deterioration from the ‘As New’ condition | 1.1 | 10 | 0.5
> 10% deterioration from New | Over 10% deterioration from the ‘As New’ condition | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 161
Condition Criteria: IR Test Results | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | The insulation test result meets the manufacturers recommended value | 1 | 10 | 0.5
Upto 10% deterioration from New | Up to 10% deterioration from the ‘As New’ condition | 1.1 | 10 | 0.5
> 10% deterioration from New | Over 10% deterioration from the ‘As New’ condition | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 162
Condition Criteria: Oil Test/ Gas Test Results | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | The oil or gas test result meets the required European Standard for new oil or gas | 1 | 10 | 0.5
Upto 10% deterioration from New | Up to 10% deterioration from the ‘As New’ condition | 1.1 | 10 | 0.5
> 10% deterioration from New | Over 10% deterioration from the ‘As New’ condition | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 163
Condition Criteria: Temperature Readings | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Ambient or Below | At or below ambient temperature | 0.9 | 10 | 0.5
Above Ambient | Above ambient temperature | 1 | 10 | 0.5
Substantially Above Ambient | Operating above the manufacturers recommended maximum temperature | 1.1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 164
Condition Criteria: Trip Timing Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Pass | Trip time within acceptable range for the type of switchgear | 1 | 10 | 0.5
Fail | Trip time slower than acceptable time for the type of switchgear | 1.4 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 165
Condition Criteria: Partial Discharge Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | Low or negligible levels of partial discharge indicating no issues identified (e.g. a green condition using a TEV or <10% of manufacturers recommendation | 1 | 10 | 0.5
Medium | Some moderate levels of partial discharge recorded (e.g. ‘Amber’ result from TEV measuring device or between 10% and 30% of the manufacturers recommendation) | 1.1 | 10 | 0.5
High (Not Confirmed) | High levels of partial discharge indicating possible defect with plant / equipment, requiring further investigation (e.g. ‘Red’ result from TEV measuring device or above manufacturers recommendation) | 1.3 | 10 | 5.5
High (Confirmed) | High partial discharge. Source of partial discharge confirmed as potential source of failure | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 166
Condition Criteria: Ductor Test Results | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | The joint test result meets the manufacturers recommended value | 1 | 10 | 0.5
Upto 10% deterioration from New | Up to 10% deterioration from the ‘As New’ condition | 1.1 | 10 | 0.5
> 10% deterioration from New | Over 10% deterioration from the ‘As New’ condition | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 167
Condition Criteria: IR Test Results | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | The insulation test result meets the manufacturers recommended value | 1 | 10 | 0.5
Upto 10% deterioration from New | Up to 10% deterioration from the ‘As New’ condition | 1.1 | 10 | 0.5
> 10% deterioration from New | Over 10% deterioration from the ‘As New’ condition | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 168
Condition Criteria: Oil Test/ Gas Test Results | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
As New | The oil or gas test result meets the required European Standard for new oil or gas | 1 | 10 | 0.5
Upto 10% deterioration from New | Up to 10% deterioration from the ‘As New’ condition | 1.1 | 10 | 0.5
> 10% deterioration from New | Over 10% deterioration from the ‘As New’ condition | 1.3 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 169
Condition Criteria: Temperature Readings | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Ambient or Below | At or below ambient temperature | 0.9 | 10 | 0.5
Above Ambient | Above ambient temperature | 1 | 10 | 0.5
Substantially Above Ambient | Operating above the manufacturers recommended maximum temperature | 1.1 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 170
Condition Criteria: Trip Timing Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Pass | Trip time within acceptable range for the type of switchgear | 1 | 10 | 0.5
Fail | Trip time slower than acceptable time for the type of switchgear | 1.4 | 10 | 0.5
Default | No data available | 1 | 10 | 0.5

## 171
Condition Criteria: Partial Discharge Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | Low or negligible levels of partial discharge indicating no issues identified (e.g. a green condition using a TEV or <10% of manufacturers recommendation | 1 | 10 | 0.5
Medium | Some moderate levels of partial discharge recorded (e.g. ‘Amber’ result from TEV measuring device or between 10% and 30% of the manufacturers recommendation) | 1.1 | 10 | 0.5
High (Not Confirmed) | High levels of partial discharge indicating possible defect with plant / equipment, requiring further investigation (e.g. ‘Red’ result from TEV measuring device or above manufacturers recommendation) | 1.3 | 10 | 5.5
High (Confirmed) | High partial discharge. Source of partial discharge confirmed as potential source of failure | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 172
Condition Criteria: Temperature Reading | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Normal | Normally expected temperature for transformer loading | 1 | 10 | 0.5
Moderately High | Slightly above normally expected temperature for transformer loading | 1.2 | 10 | 0.5
Very High | Significantly above normally expected temperature for transformer loading | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 173
Condition Criteria: Partial Discharge Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | Low or negligible levels of partial discharge indicating no issues identified (e.g. a green condition using a TEV or <10% of manufacturers recommendation | 1 | 10 | 0.5
Medium | Some moderate levels of partial discharge recorded (e.g. ‘Amber’ result from TEV measuring device or between 10% and 30% of the manufacturers recommendation) | 1.1 | 10 | 0.5
High (Not Confirmed) | High levels of partial discharge indicating possible defect with plant / equipment, requiring further investigation (e.g. ‘Red’ result from TEV measuring device or above manufacturers recommendation) | 1.3 | 10 | 5.5
High (Confirmed) | High partial discharge. Source of partial discharge confirmed as potential source of failure | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 174
Condition Criteria: Temperature Reading | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Normal | Normally expected temperature for transformer loading | 1 | 10 | 0.5
Moderately High | Slightly above normally expected temperature for transformer loading | 1.2 | 10 | 0.5
Very High | Significantly above normally expected temperature for transformer loading | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 175
Condition Criteria: Partial Discharge Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | Low or negligible levels of partial discharge indicating no issues identified (e.g. a green condition using a TEV or <10% of manufacturers recommendation | 1 | 10 | 0.5
Medium | Some moderate levels of partial discharge recorded (e.g. ‘Amber’ result from TEV measuring device or between 10% and 30% of the manufacturers recommendation) | 1.1 | 10 | 0.5
High (Not Confirmed) | High levels of partial discharge indicating possible defect with plant / equipment, requiring further investigation (e.g. ‘Red’ result from TEV measuring device or above manufacturers recommendation) | 1.3 | 10 | 5.5
High (Confirmed) | High partial discharge. Source of partial discharge confirmed as potential source of failure | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 176
Condition Criteria: Partial Discharge Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | Low or negligible levels of partial discharge indicating no issues identified (e.g. a green condition using a TEV or <10% of manufacturers recommendation | 1 | 10 | 0.5
Medium | Some moderate levels of partial discharge recorded (e.g. ‘Amber’ result from TEV measuring device or between 10% and 30% of the manufacturers recommendation) | 1.1 | 10 | 0.5
High (Not Confirmed) | High levels of partial discharge indicating possible defect with plant / equipment, requiring further investigation (e.g. ‘Red’ result from TEV measuring device or above manufacturers recommendation) | 1.3 | 10 | 5.5
High (Confirmed) | High partial discharge. Source of partial discharge confirmed as potential source of failure | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 177
Condition Criteria: Temperature Reading | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Normal | Normally expected temperature for transformer loading | 1 | 10 | 0.5
Moderately High | Slightly above normally expected temperature for transformer loading | 1.2 | 10 | 0.5
Very High | Significantly above normally expected temperature for transformer loading | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 178
Condition Criteria: Partial Discharge Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | Low or negligible levels of partial discharge indicating no issues identified (e.g. a green condition using a TEV or <10% of manufacturers recommendation | 1 | 10 | 0.5
Medium | Some moderate levels of partial discharge recorded (e.g. ‘Amber’ result from TEV measuring device or between 10% and 30% of the manufacturers recommendation) | 1.1 | 10 | 0.5
High (Not Confirmed) | High levels of partial discharge indicating possible defect with plant / equipment, requiring further investigation (e.g. ‘Red’ result from TEV measuring device or above manufacturers recommendation) | 1.3 | 10 | 5.5
High (Confirmed) | High partial discharge. Source of partial discharge confirmed as potential source of failure | 1.5 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 179
Condition Criteria: Sheath Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Pass | Satisfactory | 1 | 10 | 0.5
Failed Minor | Failure requiring minor repair | 1.3 | 10 | 0.5
Failed Major | Unacceptable Sheath Leakage or Condition | 1.6 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 180
Condition Criteria: Partial Discharge Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | No unusual activity detected | 1 | 10 | 0.5
Medium | PD detected requiring regular monitoring | 1.15 | 10 | 0.5
High | Intervention required | 1.5 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 181
Lower | Upper | Bound Description | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No historic faults recorded | No historic faults recorded | Condition Criteria: Fault Rate ( faults per annum) per km | No recorded faults or failures in the period | 1 | 5.4 | 0.5
0 | 0.01 | Condition Criteria: Fault Rate ( faults per annum) per km | The calculated fault rate for the asset in the period | 1.3 | 10 | 0.5
0.01 | 0.1 | Condition Criteria: Fault Rate ( faults per annum) per km | The calculated fault rate for the asset in the period | 1.6 | 10 | 5.5
0.1 |  | Condition Criteria: Fault Rate ( faults per annum) per km | The calculated fault rate for the asset in the period | 1.8 | 10 | 8
Default | Default | Condition Criteria: Fault Rate ( faults per annum) | No data available | 1 | 10 | 0.5

## 182
Condition Criteria: Leakage Rate | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No (or very low) historic leakage recorded | No or negligible levels of leakage | 1 | 10 | 0.5
Low/ moderate | Requires occasional intervention to maintain pressure | 1.3 | 10 | 0.5
High | Requires regular intervention to maintain pressure | 1.8 | 10 | 5.5
Very High | Requires intervention at the point of oil loss | 2 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 183
Condition Criteria: Leakage Rate | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No (or very low) historic leakage recorded | No or negligible levels of leakage | 1 | 10 | 0.5
Low/ moderate | Requires occasional intervention to maintain pressure | 1.3 | 10 | 0.5
High | Requires regular intervention to maintain pressure | 1.8 | 10 | 5.5
Very High | Requires intervention at the point of gas loss | 2 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 184
Condition Criteria: Sheath Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Pass | Satisfactory | 1 | 10 | 0.5
Failed Minor | Failure requiring minor repair | 1.3 | 10 | 0.5
Failed Major | Unacceptable sheath leakage or condition | 1.6 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 185
Condition Criteria: Partial Discharge Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | No unusual activity detected | 1 | 10 | 0.5
Medium | PD detected requiring regular monitoring | 1.15 | 10 | 0.5
High | Intervention required | 1.5 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 186
Lower | Upper | Bound Description | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No historic faults recorded | No historic faults recorded | Condition Criteria: Fault Rate (faults per annum) per km | No recorded faults or failures in the period | 1 | 5.4 | 0.5
0 | 0.01 | Condition Criteria: Fault Rate (faults per annum) per km | The calculated fault rate for the asset in the period | 1.3 | 10 | 0.5
0.01 | 0.1 | Condition Criteria: Fault Rate (faults per annum) per km | The calculated fault rate for the asset in the period | 1.6 | 10 | 5.5
0.1 |  | Condition Criteria: Fault Rate (faults per annum) per km | The calculated fault rate for the asset in the period | 1.8 | 10 | 8
Default | Default | Condition Criteria: Fault Rate (faults per annum) | No data available | 1 | 10 | 0.5

## 187
Condition Criteria: Leakage Rate | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No (or very low) historic leakage recorded | No or negligible levels of leakage | 1 | 10 | 0.5
Low/ moderate | Requires occasional intervention to maintain pressure | 1.3 | 10 | 0.5
High | Requires regular intervention to maintain pressure | 1.8 | 10 | 5.5
Very High | Requires intervention at the point of gas loss | 2 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 188
Condition Criteria: Leakage Rate | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No (or very low) historic leakage recorded | No or negligible levels of leakage | 1 | 10 | 0.5
Low/ moderate | Requires occasional intervention to maintain pressure | 1.3 | 10 | 0.5
High | Requires regular intervention to maintain pressure | 1.8 | 10 | 5.5
Very High | Requires intervention at the point of gas loss | 2 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 189
Condition Criteria: Sheath Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Pass | Satisfactory | 1 | 10 | 0.5
Failed Minor | Failure requiring minor repair | 1.3 | 10 | 0.5
Failed Major | Unacceptable sheath leakage or condition | 1.6 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 190
Condition Criteria: Partial Discharge Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | No unusual activity detected | 1 | 10 | 0.5
Medium | PD detected requiring regular monitoring | 1.15 | 10 | 0.5
High | Intervention required | 1.5 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 191
Lower | Upper | Bound Description | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
No historic faults recorded | No historic faults recorded | Condition Criteria: Fault Rate ( faults per annum) per km | No recorded faults or failures in the period | 1 | 5.4 | 0.5
0 | 0.01 | Condition Criteria: Fault Rate ( faults per annum) per km | The calculated fault rate for the asset in the period | 1.3 | 10 | 0.5
0.01 | 0.1 | Condition Criteria: Fault Rate ( faults per annum) per km | The calculated fault rate for the asset in the period | 1.6 | 10 | 5.5
0.1 |  | Condition Criteria: Fault Rate ( faults per annum) per km | The calculated fault rate for the asset in the period | 1.8 | 10 | 8
Default | Default | Condition Criteria: Fault Rate ( faults per annum) | No data available | 1 | 10 | 0.5

## 192
Condition Criteria: Degree of Decay/Deterioration | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
None | Zero measured loss of strength | 0.8 | 5.4 | 0.5
No Significant Decay/Deterioration | Minor loss of strength | 1 | 6.4 | 0.5
High | Significant loss of residual strength, still within acceptable level | 1.4 | 10 | 5.5
Very High | Residual strength below acceptable level | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 193
Condition Criteria: Degree of Decay/Deterioration | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
None | Zero measured loss of strength | 0.8 | 5.4 | 0.5
No Significant Decay/Deterioration | Minor loss of strength | 1 | 6.4 | 0.5
High | Significant loss of residual strength, still within acceptable level | 1.4 | 10 | 5.5
Very High | Residual strength below acceptable level | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 194
Condition Criteria: Degree of Decay/Deterioration | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
None | Zero measured loss of strength | 0.8 | 5.4 | 0.5
No Significant Decay/Deterioration | Minor loss of strength | 1 | 6.4 | 0.5
High | Significant loss of residual strength, still within acceptable level | 1.4 | 10 | 5.5
Very High | Residual strength below acceptable level | 1.8 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 195
Condition Criteria: Thermal Imaging Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | Ambient plus or minus 100C | 1 | 5.4 | 0.5
Medium | Ambient plus 10 - 250C | 1.1 | 10 | 0.5
High | Ambient plus more than 250C | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 196
Condition Criteria: Ductor Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | As commissioned or up to 2.5% variance | 1 | 5.4 | 0.5
Medium | As commissioned or up to 5% variance | 1.1 | 10 | 0.5
High | As commissioned or over 5% variance | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 197
Condition Criteria: Thermal Imaging Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | Ambient plus or minus 100C | 1 | 5.4 | 0.5
Medium | Ambient plus 10 - 250C | 1.1 | 10 | 0.5
High | Ambient plus more than 250C | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 198
Condition Criteria: Ductor Test Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | As commissioned or up to 2.5% variance | 1 | 5.4 | 0.5
Medium | As commissioned or up to 5% variance | 1.1 | 10 | 0.5
High | As commissioned or over 5% variance | 1.4 | 10 | 5.5
Default | No data available | 1 | 10 | 0.5

## 199
Condition Criteria: Conductor Sampling Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | No obvious or minor deterioration | 1 | 5.4 | 0.5
Medium/Normal | Wear is consistent with the duty and environment of the circuit | 1.1 | 10 | 3
High | Wear indicated that an end of life condition exists | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 200
Condition Criteria: Corrosion Monitoring Survey Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | No obvious or minor deterioration | 1 | 5.4 | 0.5
Medium/Normal | Wear is consistent with the duty and environment of the circuit | 1.1 | 10 | 3
High | Wear indicated that an end of life condition exists | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 201
Condition Criteria: Conductor Sampling Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | No obvious or minor deterioration | 1 | 5.4 | 0.5
Medium/Normal | Wear is consistent with the duty and environment of the circuit | 1.1 | 10 | 3
High | Wear indicated that an end of life condition exists | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 202
Condition Criteria: Corrosion Monitoring Survey Result | Description | Condition Input Factor | Condition Input Cap | Condition Input Collar
Low | No obvious or minor deterioration | 1 | 5.4 | 0.5
Medium/Normal | Wear is consistent with the duty and environment of the circuit | 1.1 | 10 | 3
High | Wear indicated that an end of life condition exists | 1.4 | 10 | 8
Default | No data available | 1 | 10 | 0.5

## 203
Lower | Upper | Bound Description | Moisture Score | Type
-0.01 | 15 | Moisture (ppm) | 0 | HV Transformer (GM)
15 | 30 | Moisture (ppm) | 2 | HV Transformer (GM)
30 | 40 | Moisture (ppm) | 4 | HV Transformer (GM)
40 | 50 | Moisture (ppm) | 8 | HV Transformer (GM)
50 | 10000 | Moisture (ppm) | 10 | HV Transformer (GM)
-0.01 | 15 | Moisture (ppm) | 0 | EHV Transformer (GM)
15 | 30 | Moisture (ppm) | 2 | EHV Transformer (GM)
30 | 40 | Moisture (ppm) | 4 | EHV Transformer (GM)
40 | 50 | Moisture (ppm) | 8 | EHV Transformer (GM)
50 | 10000 | Moisture (ppm) | 10 | EHV Transformer (GM)
-0.01 | 15 | Moisture (ppm) | 0 | 132kV Transformer (GM)
15 | 20 | Moisture (ppm) | 2 | 132kV Transformer (GM)
20 | 30 | Moisture (ppm) | 4 | 132kV Transformer (GM)
30 | 40 | Moisture (ppm) | 8 | 132kV Transformer (GM)
40 | 10000 | Moisture (ppm) | 10 | 132kV Transformer (GM)

## 204
Lower | Upper | Bound Description | Acidity Score | Type
-0.01 | 0.15 | Acidity (mg KOH/g) | 2 | HV Transformer (GM)
0.15 | 0.3 | Acidity (mg KOH/g) | 4 | HV Transformer (GM)
0.3 | 0.5 | Acidity (mg KOH/g) | 8 | HV Transformer (GM)
0.5 | 10000 | Acidity (mg KOH/g) | 10 | HV Transformer (GM)
-0.01 | 0.1 | Acidity (mg KOH/g) | 0 | EHV Transformer (GM)
0.1 | 0.15 | Acidity (mg KOH/g) | 2 | EHV Transformer (GM)
0.15 | 0.3 | Acidity (mg KOH/g) | 4 | EHV Transformer (GM)
0.3 | 0.4 | Acidity (mg KOH/g) | 8 | EHV Transformer (GM)
0.4 | 10000 | Acidity (mg KOH/g) | 10 | EHV Transformer (GM)
-0.01 | 0.05 | Acidity (mg KOH/g) | 0 | 132kV Transformer (GM)
0.05 | 0.1 | Acidity (mg KOH/g) | 2 | 132kV Transformer (GM)
0.1 | 0.2 | Acidity (mg KOH/g) | 4 | 132kV Transformer (GM)
0.2 | 0.3 | Acidity (mg KOH/g) | 8 | 132kV Transformer (GM)
0.3 | 10000 | Acidity (mg KOH/g) | 10 | 132kV Transformer (GM)

## 205
Lower | Upper | Bound Description | BD Strength Score | Type
-0.01 | 30 | BD Strength (kV) | 10 | HV Transformer (GM)
30 | 40 | BD Strength (kV) | 4 | HV Transformer (GM)
40 | 50 | BD Strength (kV) | 2 | HV Transformer (GM)
50 | 10000 | BD Strength (kV) | 0 | HV Transformer (GM)
-0.01 | 30 | BD Strength (kV) | 10 | EHV Transformer (GM)
30 | 40 | BD Strength (kV) | 4 | EHV Transformer (GM)
40 | 50 | BD Strength (kV) | 2 | EHV Transformer (GM)
50 | 10000 | BD Strength (kV) | 0 | EHV Transformer (GM)
-0.01 | 40 | BD Strength (kV) | 10 | 132kV Transformer (GM)
40 | 50 | BD Strength (kV) | 4 | 132kV Transformer (GM)
50 | 60 | BD Strength (kV) | 2 | 132kV Transformer (GM)
60 | 10000 | BD Strength (kV) | 0 | 132kV Transformer (GM)

## 206
Lower | Upper | Bound Description | Oil Test Factor | Type
-0.01 | 250 | Oil Condition Score | 1 | HV Transformer (GM)
250 | 500 | Oil Condition Score | 1.1 | HV Transformer (GM)
500 | 1000 | Oil Condition Score | 1.2 | HV Transformer (GM)
1000 | 10000 | Oil Condition Score | 1.4 | HV Transformer (GM)
-0.01 | 50 | Oil Condition Score | 0.9 | EHV Transformer (GM)
50 | 200 | Oil Condition Score | 1 | EHV Transformer (GM)
200 | 500 | Oil Condition Score | 1.05 | EHV Transformer (GM)
500 | 1000 | Oil Condition Score | 1.1 | EHV Transformer (GM)
1000 | 10000 | Oil Condition Score | 1.2 | EHV Transformer (GM)
-0.01 | 50 | Oil Condition Score | 0.9 | 132kV Transformer (GM)
50 | 200 | Oil Condition Score | 1 | 132kV Transformer (GM)
200 | 500 | Oil Condition Score | 1.05 | 132kV Transformer (GM)
500 | 1000 | Oil Condition Score | 1.1 | 132kV Transformer (GM)
1000 | 10000 | Oil Condition Score | 1.2 | 132kV Transformer (GM)

## 207
Lower | Upper | Bound Description | Oil Test Collar | Type
0.5
-0.01 | 250 | Oil Condition Score | 0.5 | HV Transformer (GM)
250 | 500 | Oil Condition Score | 0.5 | HV Transformer (GM)
500 | 1000 | Oil Condition Score | 0.5 | HV Transformer (GM)
1000 | 10000 | Oil Condition Score | 5.5 | HV Transformer (GM)
-0.01 | 50 | Oil Condition Score | 0.5 | EHV Transformer (GM)
50 | 200 | Oil Condition Score | 0.5 | EHV Transformer (GM)
200 | 500 | Oil Condition Score | 0.5 | EHV Transformer (GM)
500 | 1000 | Oil Condition Score | 0.5 | EHV Transformer (GM)
1000 | 10000 | Oil Condition Score | 5.5 | EHV Transformer (GM)
-0.01 | 50 | Oil Condition Score | 0.5 | 132kV Trabsformer (GM)
50 | 200 | Oil Condition Score | 0.5 | 132kV Trabsformer (GM)
200 | 500 | Oil Condition Score | 0.5 | 132kV Trabsformer (GM)
500 | 1000 | Oil Condition Score | 0.5 | 132kV Trabsformer (GM)
1000 | 10000 | Oil Condition Score | 5.5 | 132kV Trabsformer (GM)

## 208
Lower | Upper | Bound Description | Hydrogen Condition State
-0.01 | 20 | Hydrogen (ppm) | 0
20 | 40 | Hydrogen (ppm) | 2
40 | 100 | Hydrogen (ppm) | 4
100 | 200 | Hydrogen (ppm) | 10
200 | 10000 | Hydrogen (ppm) | 16

## 209
Lower | Upper | Bound Description | Methane Condition State
-0.01 | 10 | Methane (ppm) | 0
10 | 20 | Methane (ppm) | 2
20 | 50 | Methane (ppm) | 4
50 | 150 | Methane (ppm) | 10
150 | 10000 | Methane (ppm) | 16

## 210
Lower | Upper | Bound Description | Ethylene Condition State
-0.01 | 10 | Ethylene (ppm) | 0
10 | 20 | Ethylene (ppm) | 2
20 | 50 | Ethylene (ppm) | 4
50 | 150 | Ethylene (ppm) | 10
150 | 10000 | Ethylene (ppm) | 16

## 211
Lower | Upper | Bound Description | Ethane Condition State
-0.01 | 10 | Ethane (ppm) | 0
10 | 20 | Ethane (ppm) | 2
20 | 50 | Ethane (ppm) | 4
50 | 150 | Ethane (ppm) | 10
150 | 10000 | Ethane (ppm) | 16

## 212
Lower | Upper | Bound Description | Acetylene Condition State
-0.01 | 1 | Acetylene (ppm) | 0
1 | 5 | Acetylene (ppm) | 2
5 | 20 | Acetylene (ppm) | 4
20 | 100 | Acetylene (ppm) | 8
100 | 10000 | Acetylene (ppm) | 10

## 213
Lower | Upper | Bound Description | Change Category
-1000 | -5 | % Change | Negative
-5 | 5 | % Change | Neutral
5 | 25 | % Change | Small
25 | 100 | % Change | Significant
100 | 1000 | % Change | Large

## 214
> % Change | DGA Test Factor
Negative | 0.9
Neutral | 1
Small | 1.1
Significant | 1.2
Large | 1.5

## 215
Lower | Upper | Bound Description | FFA Test Factor
-0.01 | 4 | FFA value (ppm) | 1
4 | 5 | FFA value (ppm) | 1.1
5 | 6 | FFA value (ppm) | 1.25
6 | 7 | FFA value (ppm) | 1.4
7 |  | FFA value (ppm) | 1.6

## 216
Lower | Upper | Bound Description | Ageing Reduction Factor
0 | 2 | Current Health Score | 1
2 | 5.5 | Current Health Score | ((Current Health Score - 2)/ 7) + 1
5.5 |  | Current Health Score | 1.5

## 217
Refurbishment Intervention Activity | Health Index Asset Category | Asset Register Category | Input Data Affected By Intervention
Complete replacement of the operating mechanism (ACB) | LV Switchgear | LV Circuit Breaker | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of complete feederway | LV Switchgear | LV Pillar (ID), LV Pillar (OD at Substation) & LV Pillars (OD not at Substation) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Complete factory refurbishment | HV Switchgear (GM) - Distribution | 6.6/11kV CB (GM) Secondary, 6.6/11kV RMU, 6.6/11kV Switch (GM), 6.6/11kV X-type RMU, 20kV CB (GM) Secondary, 20kV RMU & 20kV Switch (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Complete Refurbishment (factory or onsite) e.g. strip down & rebuild, replacing all worn parts | HV Switchgear (GM) - Distribution | 6.6/11kV CB (GM) Secondary, 6.6/11kV RMU, 6.6/11kV Switch (GM), 6.6/11kV X-type RMU, 20kV CB (GM) Secondary, 20kV RMU & 20kV Switch (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Complete replacement of the operating mechanism | HV Switchgear (GM) - Distribution | 6.6/11kV CB (GM) Secondary, 6.6/11kV RMU, 6.6/11kV Switch (GM), 6.6/11kV X-type RMU, 20kV CB (GM) Secondary, 20kV RMU & 20kV Switch (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of cable boxes | HV Switchgear (GM) - Distribution | 6.6/11kV CB (GM) Secondary, 6.6/11kV RMU, 6.6/11kV Switch (GM), 6.6/11kV X-type RMU, 20kV CB (GM) Secondary, 20kV RMU & 20kV Switch (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of the moving portion (truck) in withdrawable equipment | HV Switchgear (GM) - Distribution | 6.6/11kV CB (GM) Secondary & 20kV CB (GM) Secondary | i) Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier; and ii) Increase the Expected Life by 20 years
Complete factory refurbishment | HV Switchgear (GM) - Primary | 6.6/11kV CB (GM) Primary & 20kV CB (GM) Primary | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Complete Refurbishment (factory or onsite) e.g. strip down & rebuild, replacing all worn parts | HV Switchgear (GM) - Primary | 6.6/11kV CB (GM) Primary & 20kV CB (GM) Primary | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Complete replacement of the operating mechanism | HV Switchgear (GM) - Primary | 6.6/11kV CB (GM) Primary & 20kV CB (GM) Primary | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of cable boxes | HV Switchgear (GM) - Primary | 6.6/11kV CB (GM) Primary & 20kV CB (GM) Primary | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of the moving portion (truck) in withdrawable equipment | HV Switchgear (GM) - Primary | 6.6/11kV CB (GM) Primary & 20kV CB (GM) Primary | i) Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier; and ii) Increase the Expected Life by 20 years
Complete Refurbishment (factory or onsite) e.g. strip down & rebuild, replacing all worn parts | EHV Switchgear (GM) | 33kV CB (Air Insulated Busbars)(ID) (GM), 33kV CB (Air Insulated Busbars)(OD) (GM), 33kV CB (Gas Insulated Busbars)(ID) (GM), 33kV CB (Gas Insulated Busbars)(OD) (GM), 33kV RMU, 33kV Switch (GM), 66kV CB (Air Insulated Busbars)(ID) (GM), 66kV CB (Air Insulated Busbars)(OD) (GM), 66kV CB (Gas Insulated Busbars)(ID) (GM) & 66kV CB (Gas Insulated Busbars)(OD) (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Complete replacement of the operating mechanism | EHV Switchgear (GM) | 33kV CB (Air Insulated Busbars)(ID) (GM), 33kV CB (Air Insulated Busbars)(OD) (GM), 33kV CB (Gas Insulated Busbars)(ID) (GM), 33kV CB (Gas Insulated Busbars)(OD) (GM), 33kV RMU, 33kV Switch (GM), 66kV CB (Air Insulated Busbars)(ID) (GM), 66kV CB (Air Insulated Busbars)(OD) (GM), 66kV CB (Gas Insulated Busbars)(ID) (GM) & 66kV CB (Gas Insulated Busbars)(OD) (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of cable boxes | EHV Switchgear (GM) | 33kV CB (Air Insulated Busbars)(ID) (GM), 33kV CB (Air Insulated Busbars)(OD) (GM), 33kV CB (Gas Insulated Busbars)(ID) (GM), 33kV CB (Gas Insulated Busbars)(OD) (GM), 33kV RMU, 33kV Switch (GM), 66kV CB (Air Insulated Busbars)(ID) (GM), 66kV CB (Air Insulated Busbars)(OD) (GM), 66kV CB (Gas Insulated Busbars)(ID) (GM) & 66kV CB (Gas Insulated Busbars)(OD) (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of the moving portion (truck) in withdrawable equipment | EHV Switchgear (GM) | 33kV CB (Air Insulated Busbars)(ID) (GM), 33kV CB (Air Insulated Busbars)(OD) (GM) & 33kV CB (Gas Insulated Busbars)(ID) (GM) | i) Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier; and ii) Increase the Expected Life by 20 years
Complete Refurbishment (factory or onsite) e.g. strip down & rebuild, replacing all worn parts | 132kV CBs | 132kV CB (Air Insulated Busbars)(ID) (GM), 132kV CB (Air Insulated Busbars)(OD) (GM), 132kV CB (Gas Insulated Busbars)(ID) (GM) & 132kV CB (Gas Insulated Busbars)(OD) (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Complete replacement of the operating mechanism | 132kV CBs | 132kV CB (Air Insulated Busbars)(ID) (GM), 132kV CB (Air Insulated Busbars)(OD) (GM), 132kV CB (Gas Insulated Busbars)(ID) (GM) & 132kV CB (Gas Insulated Busbars)(OD) (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of cable boxes | 132kV CBs | 132kV CB (Air Insulated Busbars)(ID) (GM), 132kV CB (Air Insulated Busbars)(OD) (GM), 132kV CB (Gas Insulated Busbars)(ID) (GM) & 132kV CB (Gas Insulated Busbars)(OD) (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Complete factory refurbishment | HV Transformer (GM) | 6.6/11kV Transformer (GM) & 20kV Transformer (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Installation of replacement windings | HV Transformer (GM) | 6.6/11kV Transformer (GM) & 20kV Transformer (GM) | i) Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier; and ii) Revise age to reflect time elapsed since Refurbishment undertaken
On site processing to recondition oil to remove moisture and acidity from windings | HV Transformer (GM) | 6.6/11kV Transformer (GM) & 20kV Transformer (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of cooling radiators | HV Transformer (GM) | 6.6/11kV Transformer (GM) & 20kV Transformer (GM) | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs and Measured Condition Inputs
Complete factory refurbishment | EHV Transformer | 33kV Transformer (GM) & 66kV Transformer | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Installation of replacement windings | EHV Transformer | 33kV Transformer (GM) & 66kV Transformer | i) Reassess Health Score Modifier for Main Transformer subcomponent by reassessing relevant Observed Condition Inputs, Measured Condition Inputs, Oil Test Modifier, DGA Test Modifier, FFA Test Modifier and Reliability Modifier; and ii) Revise age to reflect time elapsed since Refurbishment undertaken
On site processing to recondition oil to remove moisture and acidity from windings | EHV Transformer | 33kV Transformer (GM) & 66kV Transformer | Reassess Health Score Modifier for Main Transformer subcomponent by reassessing Oil Test Modifier
Replacement of bushings | EHV Transformer | 33kV Transformer (GM) & 66kV Transformer | Reassess Health Score Modifier for Main Transformer subcomponent by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of cooling radiators | EHV Transformer | 33kV Transformer (GM) & 66kV Transformer | Reassess Health Score Modifier for Main Transformer subcomponent by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of gaskets & seals | EHV Transformer | 33kV Transformer (GM) & 66kV Transformer | Reassess Health Score Modifier for Main Transformer subcomponent by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of Tapchangers or full replacement of Tapchanger mechanism | EHV Transformer | 33kV Transformer (GM) & 66kV Transformer | i) Reassess Health Score Modifier for Tapchanger subcomponent by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier; and ii) Where Tapchanger is replaced: revise age of Tapchanger subcomponent, used in the calculation of Initial Health Score, to the age of the new Tapchanger
Complete factory refurbishment | 132kV Transformer | 132kV Transformer | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Installation of replacement windings | 132kV Transformer | 132kV Transformer | i) Reassess Health Score Modifier for Main Transformer subcomponent by reassessing relevant Observed Condition Inputs, Measured Condition Inputs, Oil Test Modifier, DGA Test Modifier, FFA Test Modifier and Reliability Modifier; and ii) Revise age to reflect time elapsed since Refurbishment undertaken
On site processing to recondition oil to remove moisture and acidity from windings | 132kV Transformer | 132kV Transformer | Reassess Health Score Modifier for Main Transformer subcomponent by reassessing Oil Test Modifier
Replacement of bushings | 132kV Transformer | 132kV Transformer | Reassess Health Score Modifier for Main Transformer subcomponent by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of cooling radiators | 132kV Transformer | 132kV Transformer | Reassess Health Score Modifier for Main Transformer subcomponent by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of gaskets & seals | 132kV Transformer | 132kV Transformer | Reassess Health Score Modifier for Main Transformer subcomponent by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier
Replacement of Tapchangers or full replacement of Tapchanger mechanism | 132kV Transformer | 132kV Transformer | i) Reassess Health Score Modifier for Tapchanger subcomponent by reassessing relevant Observed Condition Inputs, Measured Condition Inputs and Reliability Modifier; and ii) Where Tapchanger is replaced: revise age of Tapchanger subcomponent, used in the calculation of Initial Health Score, to the age of the new Tapchanger
Pole Strengthening (e.g. clamping a steelwork supporting bracket to an existing pole) | LV Poles | LV Poles | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs and Measured Condition Inputs
Small footprint steel masts: Replacement of individual steelwork members | LV Poles | LV Poles | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs and Measured Condition Inputs
Pole Strengthening (e.g. clamping a steelwork supporting bracket to an existing pole) | HV Poles | 6.6/11kV Poles & 20kV Poles | Reassess Health Score Modifier by reassessing Pole Decay/Deterioration Measured Condition Inputs
Small footprint steel masts: Replacement of individual steelwork members | HV Poles | 6.6/11kV Poles & 20kV Poles | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs and Measured Condition Inputs
Pole Strengthening (e.g. clamping a steelwork supporting bracket to an existing pole) | EHV Pole | 33kV Pole & 66kV Pole | Reassess Health Score Modifier by reassessing Pole Decay/Deterioration Measured Condition Inputs
Small footprint steel masts: Replacement of individual steelwork members | EHV Pole | 33kV Pole & 66kV Pole | Reassess Health Score Modifier by reassessing relevant Observed Condition Inputs and Measured Condition Inputs
Painting of Tower | EHV Tower | 33kV Tower & 66kV Tower | i) Reassess Health Score Modifier for Tower Paintwork subcomponent by reassessing Paintwork Condition Input; and ii) revise age of Tower Paintwork subcomponent, used in the calculation of Initial Health Score, to the time elapsed since the Tower was most recently painted
Replacement of individual steelwork members | EHV Tower | 33kV Tower & 66kV Tower | Reassess Health Score Modifier for the Tower Steelwork subcomponent by reassessing relevant Observed Condition Inputs
Replacement of Tower foundations | EHV Tower | 33kV Tower & 66kV Tower | Reassess Health Score Modifier for the Tower Foundation subcomponent by reassessing relevant Observed Condition Inputs
Painting of Tower | 132kV Tower | 132kV Tower | i) Reassess Health Score Modifier for Tower Paintwork subcomponent by reassessing Paintwork Condition Input ii) revise age of Tower Paintwork subcomponent, used in the calculation of Initial Health Score, to the time elapsed since the Tower was most recently painted
Replacement of individual steelwork members | 132kV Tower | 132kV Tower | Reassess Health Score Modifier for the Tower Steelwork subcomponent by reassessing relevant Observed Condition Inputs
Replacement of Tower foundations | 132kV Tower | 132kV Tower | Reassess Health Score Modifier for the Tower Foundation subcomponent by reassessing relevant Observed Condition Inputs
Re-engineering (replacement/refurbishment/relocation) of pressurising system equipment with the objective of reducing the normal operating fluid pressure in the cable system | EHV Cable (Gas) | 33kV UG Cable (Gas) & 66kV UG Cable (Gas) | Reassess Health Score Modifier by reassessing relevant Measured Condition Inputs (incl. Leakage Rate Condition Input)
Remaking existing joints and terminations in situ | EHV Cable (Gas) | 33kV UG Cable (Gas) & 66kV UG Cable (Gas) | Reassess Health Score Modifier by reassessing relevant Measured Condition Inputs (incl. Leakage Rate Condition Input)
Replacement of cable joints and terminations (including sealing ends) | EHV Cable (Gas) | 33kV UG Cable (Gas) & 66kV UG Cable (Gas) | Reassess Health Score Modifier by reassessing relevant Measured Condition Inputs (incl. Leakage Rate Condition Input)
Re-engineering (replacement/refurbishment/relocation) of pressurising system equipment with the objective of reducing the normal operating fluid pressure in the cable system | EHV Cable (Oil) | 33kV UG Cable (Oil) & 66kV UG Cable (Oil) | Reassess Health Score Modifier by reassessing relevant Measured Condition Inputs (incl. Leakage Rate Condition Input)
Remaking existing joints and terminations in situ | EHV Cable (Oil) | 33kV UG Cable (Oil) & 66kV UG Cable (Oil) | Reassess Health Score Modifier by reassessing relevant Measured Condition Inputs (incl. Leakage Rate Condition Input)
Replacement of cable joints and terminations (including sealing ends) | EHV Cable (Oil) | 33kV UG Cable (Oil) & 66kV UG Cable (Oil) | Reassess Health Score Modifier by reassessing relevant Measured Condition Inputs (incl. Leakage Rate Condition Input)
Re-engineering (replacement/refurbishment/relocation) of pressurising system equipment with the objective of reducing the normal operating fluid pressure in the cable system | 132kV Cable (Gas) | 132kV UG Cable (Gas) | Reassess Health Score Modifier by reassessing relevant Measured Condition Inputs (incl. Leakage Rate Condition Input)
Remaking existing joints and terminations in situ | 132kV Cable (Gas) | 132kV UG Cable (Gas) | Reassess Health Score Modifier by reassessing relevant Measured Condition Inputs (incl. Leakage Rate Condition Input)
Replacement of cable joints and terminations (including sealing ends) | 132kV Cable (Gas) | 132kV UG Cable (Gas) | Reassess Health Score Modifier by reassessing relevant Measured Condition Inputs (incl. Leakage Rate Condition Input)
Re-engineering (replacement/refurbishment/relocation) of pressurising system equipment with the objective of reducing the normal operating fluid pressure in the cable system | 132kV Cable (Oil) | 132kV UG Cable (Oil) | Reassess Health Score Modifier by reassessing relevant Measured Condition Inputs (incl. Leakage Rate Condition Input)
Remaking existing joints and terminations in situ | 132kV Cable (Oil) | 132kV UG Cable (Oil) | Reassess Health Score Modifier by reassessing relevant Measured Condition Inputs (incl. Leakage Rate Condition Input)
Replacement of cable joints and terminations (including sealing ends) | 132kV Cable (Oil) | 132kV UG Cable (Oil) | Reassess Health Score Modifier by reassessing "relevant Measured Condition Inputs (incl. Leakage Rate" Condition Input)

## 218
Asset Register Category | Relative Proportion Of Failure Modes (as a % of total Functional Failures) - I | Relative Proportion Of Failure Modes (as a % of total Functional Failures) - D | Relative Proportion Of Failure Modes (as a % of total Functional Failures) - C | Likely Cost of Failure - I (GBP) | Likely Cost of Failure - D (GBP) | Likely Cost of Failure - C4 (GBP) | Reference Financial Cose of Failure (GBP)
LV Poles | 20 | 70 | 10 | 163 | 1631 | 1631 | 1337
6.6/11kV Poles | 20 | 70 | 10 | 233 | 2333 | 2333 | 1913
20kV Poles | 20 | 70 | 10 | 280 | 2799 | 2799 | 2295
33kV Pole | 20 | 70 | 10 | 300 | 3007 | 3007 | 2466
66kV Pole | 20 | 70 | 10 | 453 | 4534 | 4534 | 3718
33kV Tower | 80 | 19.95 | 0.05 | 5177 | 12942 | 51771 | 6749
66kV Tower | 80 | 19.95 | 0.05 | 9700 | 24251 | 97000 | 12647
132kV Tower | 80 | 19.95 | 0.05 | 11216 | 28041 | 112163 | 14623
33kV Fittings | 80 | 15 | 5 | 136 | 339 | 1353 | 227
66kV Fittings | 80 | 15 | 5 | 174 | 436 | 1742 | 292
132kV Fittings | 80 | 15 | 5 | 290 | 724 | 2896 | 485
33kV OHL (Tower Line) Conductor | 0 | 85 | 15 | 0 | 15472 | 30945 | 17793
66kV OHL Conductor | 0 | 85 | 15 | 0 | 20522 | 41043 | 23600
132kV OHL (Tower Line) Conductor | 0 | 85 | 15 | 0 | 17746 | 35493 | 20408
HV Sub Cable | 0 | 0 | 100 | 3640 | 9100 | 81996 | 181996
33kV UG Cable (Non Pressurised) | 0 | 0 | 100 | 3164 | 7911 | 31644 | 31644
33kV UG Cable (Oil) | 99 | 0.09 | 0.01 | 120 | 7911 | 31644 | 129
33kV UG Cable (Gas) | 99 | 0.5 | 0.5 | 120 | 7911 | 31644 | 317
66kV UG Cable (Non Pressurised) | 0 | 0 | 100 | 6402 | 16006 | 64021 | 64021
66kV UG Cable (Oil) | 99 | 0.09 | 0.01 | 120 | 16006 | 64021 | 140
66kV UG Cable (Gas) | 99 | 0.5 | 0.5 | 120 | 16006 | 64021 | 519
132kV UG Cable (Non Pressurised) | 0 | 0 | 100 | 10924 | 27310 | 109244 | 109244
132kV UG Cable (Oil) | 99 | 0.09 | 0.01 | 120 | 27310 | 109244 | 154
132kV UG Cable (Gas) | 99 | 0.5 | 0.5 | 120 | 27310 | 109244 | 802
EHV Sub Cable | 0 | 0 | 100 | 5706 | 14266 | 285322 | 285322
132kV Sub Cable | 0 | 0 | 100 | 9611 | 24027 | 480542 | 480542
LV Circuit Breaker | 15 | 25 | 60 | 601 | 1502 | 6007 | 4070
LV Pillar (ID) | 15 | 25 | 60 | 837 | 2092 | 8367 | 5669
LV Pillar (OD at Substation) | 15 | 25 | 60 | 911 | 2277 | 9107 | 6170
LV UGB & LV Pillars (OD not at Substation) | 15 | 25 | 60 | 506 | 1265 | 5061 | 3429
LV Board (WM) | 15 | 25 | 60 | 1156 | 2890 | 11562 | 7833
LV Board (X-type Network) (WM) | 15 | 25 | 60 | 1365 | 3411 | 13644 | 9244
6.6/11kV CB (GM) Primary | 45 | 50 | 5 | 3348 | 8621 | 34485 | 7586
6.6/11kV CB (GM) Secondary | 15 | 25 | 60 | 1027 | 2567 | 10272 | 8000
6.6/11kV Switch (GM) | 15 | 25 | 60 | 777 | 1944 | 7774 | 5267
6.6/11kV RMU | 15 | 25 | 60 | 1452 | 3630 | 14523 | 9839
6.6/11kV X-type RMU | 15 | 25 | 60 | 1965 | 4914 | 19652 | 13314
20kV CB (GM) Primary | 45 | 50 | 5 | 4320 | 10800 | 43202 | 13314
20kV CB (GM) Secondary | 15 | 25 | 60 | 1064 | 2662 | 10648 | 7214
20kV Switch (GM) | 15 | 25 | 60 | 901 | 2253 | 9010 | 6104
20kV RMU | 15 | 25 | 60 | 1479 | 3699 | 14795 | 10024
33kV CB (Air Insulated Busbars)(ID) (GM) | 45 | 50 | 5 | 6597 | 16492 | 65971 | 14513
33kV CB (Air Insulated Busbars)(OD) (GM) | 45 | 50 | 5 | 8122 | 20307 | 81224 | 17870
33kV CB (Gas Insulated Busbars)(ID) (GM) | 45 | 50 | 5 | 9993 | 24981 | 99924 | 21984
33kV CB (Gas Insulated Busbars)(OD) (GM) | 45 | 50 | 5 | 9993 | 24981 | 99924 | 21984
33kV Switch (GM) | 45 | 50 | 5 | 4662 | 11656 | 46621 | 10257
33kV RMU | 45 | 50 | 5 | 11521 | 28804 | 115214 | 25347
66kV CB (Air Insulated Busbars)(ID) (GM) | 45 | 50 | 5 | 13150 | 32875 | 131499 | 28930
66kV CB (Air Insulated Busbars)(OD) (GM) | 45 | 50 | 5 | 21024 | 52559 | 210237 | 46252
66kV CB (Gas Insulated Busbars)(ID) (GM) | 45 | 50 | 5 | 23716 | 59291 | 237163 | 52176
66kV CB (Gas Insulated Busbars)(OD) (GM) | 45 | 50 | 5 | 23716 | 59291 | 237163 | 52176
132kV CB (Air Insulated Busbars)(ID) (GM) | 45 | 50 | 5 | 36860 | 92150 | 368601 | 81092
132kV CB (Air Insulated Busbars)(OD) (GM) | 45 | 50 | 5 | 17355 | 43387 | 173549 | 38181
132kV CB (Gas Insulated Busbars)(ID) (GM) | 45 | 50 | 5 | 76769 | 191923 | 767691 | 168892
132kV CB (Gas Insulated Busbars)(OD) (GM) | 45 | 50 | 5 | 76769 | 191923 | 767691 | 168892
6.6/11kV Transformer (GM) | 15 | 25 | 60 | 1372 | 3431 | 13722 | 9297
20kV Transformer (GM) | 15 | 25 | 60 | 1563 | 3906 | 15624 | 10585
33kV Transformer (GM) | 45 | 50 | 5 | 39863 | 99657 | 398629 | 87698
Transformador 34kV (GM) | 45 | 50 | 5 | 39863 | 99657 | 398629 | 87698
66kV Transformer | 45 | 50 | 5 | 61270 | 153178 | 612709 | 134796
132kV Transformer | 45 | 50 | 5 | 119552 | 298880 | 1195522 | 263015

## 219
Asset Register Category | Type Financial Factor Criteria | Lower | Upper | Bound Description | Type Financial Factor
LV Poles | Pole (excluding terminal poles) |  |  |  | 1
LV Poles | Pole (terminal poles) |  |  |  | 1.2
LV Poles | Steel Poles |  |  |  | 2
LV Board (WM) | Non Asbestos clad |  |  |  | 1
LV Board (WM) | Asbestos clad |  |  |  | 2
LV Board (X-type Network) (WM) | Non Asbestos clad |  |  |  | 1
LV Board (X-type Network) (WM) | Asbestos clad |  |  |  | 2
6.6/11kV Poles | Pole (supporting conductor only) |  |  |  | 1
6.6/11kV Poles | Pole (supporting plant or equipment) |  |  |  | 1.7
6.6/11kV Poles | Small footprint steel masts |  |  |  | 2
20kV Poles | Pole (supporting conductor only) |  |  |  | 1
20kV Poles | Pole (supporting plant or equipment) |  |  |  | 1.7
20kV Poles | Small footprint steel masts |  |  |  | 2
33kV Pole | Pole (supporting conductor only) |  |  |  | 1
33kV Pole | Pole (supporting plant or equipment) |  |  |  | 1.7
33kV Pole | Small footprint steel masts |  |  |  | 2
66kV Pole | Pole (supporting conductor only) |  |  |  | 1
66kV Pole | Pole (supporting plant or equipment) |  |  |  | 1.7
66kV Pole | Small footprint steel masts |  |  |  | 2
33kV Tower | Suspension |  |  |  | 1
33kV Tower | Tension |  |  |  | 1.05
33kV Tower | Terminal |  |  |  | 1.1
66kV Tower | Suspension |  |  |  | 1
66kV Tower | Tension |  |  |  | 1.05
66kV Tower | Terminal |  |  |  | 1.1
33kV Fittings | Suspension |  |  |  | 1
33kV Fittings | Tension |  |  |  | 2
66kV Fittings | Suspension |  |  |  | 1
66kV Fittings | Tension |  |  |  | 2
132kV Fittings | Suspension |  |  |  | 1
132kV Fittings | Tension |  |  |  | 2
132kV Tower | Suspension |  |  |  | 1
132kV Tower | Tension |  |  |  | 1.05
132kV Tower | Terminal |  |  |  | 1.1
6.6/11kV Transformer (GM) |  | 0 | 500 | kVA | 0.85
6.6/11kV Transformer (GM) |  | 500 | 750 | kVA | 1
6.6/11kV Transformer (GM) |  | 750 |  | kVA | 1.15
20kV Transformer (GM) |  | 0 | 500 | kVA | 0.85
20kV Transformer (GM) |  | 500 | 750 | kVA | 1
20kV Transformer (GM) |  | 750 |  | kVA | 1.15
33kV Transformer (GM) | 33/20kV, CMR equivalent | 0 | 10 | MVA, CMR equivalent | 1
33kV Transformer (GM) | 33/20kV, CMR equivalent | 10 | 20 | MVA, CMR equivalent | 1.1
33kV Transformer (GM) | 33/20kV, CMR equivalent | 20 |  | MVA, CMR equivalent | 1.25
33kV Transformer (GM) | 33/11 or 6.6kV, CMR equivalent | 0 | 10 | MVA, CMR equivalent | 0.9
33kV Transformer (GM) | 33/11 or 6.6kV, CMR equivalent | 10 | 20 | MVA, CMR equivalent | 1
33kV Transformer (GM) | 33/11 or 6.6kV, CMR equivalent | 20 |  | MVA, CMR equivalent | 1.1
Transformador 34kV (GM) | 33/20kV, CMR equivalent | 0 | 10 | MVA, CMR equivalent | 1
Transformador 34kV (GM) | 33/20kV, CMR equivalent | 10 | 20 | MVA, CMR equivalent | 1.1
Transformador 34kV (GM) | 33/20kV, CMR equivalent | 20 |  | MVA, CMR equivalent | 1.25
Transformador 34kV (GM) | 33/11 or 6.6kV, CMR equivalent | 0 | 10 | MVA, CMR equivalent | 0.9
Transformador 34kV (GM) | 33/11 or 6.6kV, CMR equivalent | 10 | 20 | MVA, CMR equivalent | 1
Transformador 34kV (GM) | 33/11 or 6.6kV, CMR equivalent | 20 |  | MVA, CMR equivalent | 1.1
66kV Transformer (GM) | 66/20kV, CMR equivalent | 0 | 10 | MVA, CMR equivalent | 1
66kV Transformer (GM) | 66/20kV, CMR equivalent | 10 | 20 | MVA, CMR equivalent | 1.1
66kV Transformer (GM) | 66/20kV, CMR equivalent | 20 |  | MVA, CMR equivalent | 1.25
66kV Transformer (GM) | 66/11 or 6.6kV, CMR equivalent | 0 | 10 | MVA, CMR equivalent | 0.9
66kV Transformer (GM) | 66/11 or 6.6kV, CMR equivalent | 10 | 20 | MVA, CMR equivalent | 1
66kV Transformer (GM) | 66/11 or 6.6kV, CMR equivalent | 20 |  | MVA, CMR equivalent | 1.1
132kV Transformer (GM) | 132/66kV | 0 | 60 | MVA | 1.05
132kV Transformer (GM) | 132/66kV | 60 |  | MVA | 1.15
132kV Transformer (GM) | 132/33kV | 0 | 60 | MVA | 0.9
132kV Transformer (GM) | 132/33kV | 60 |  | MVA | 1
66kV Transformer (GM) | 66/33kV |  |  |  | 1.1
66kV Transformer (GM) | 66/11/11kV |  |  |  | 1.1
132kV Transformer (GM) | 132/11/11kV |  |  |  | 1.1
132kV Transformer (GM) | 132/11kV |  |  |  | 0.85
132kV Transformer (GM) | 132/20kV |  |  |  | 0.95
132kV Transformer (GM) | 132/20/20kV |  |  |  | 1.1

## 220
Asset Category | Access Factor: Type A Criteria - Normal Access ( & Default Value) | Access Factor: Type B Criteria - Major Crossing (e.g. associated span crosses railway line, major road, large waterway etc.)
LV OHL Support | 1 | 3
HV OHL Support - Poles | 1 | 3
EHV OHL Support - Poles | 1 | 3
EHV OHL Support - Towers | 1 | 1.5
EHV OHL Fittings (Tower Lines) | 1 | 2
EHV OHL Conductors (Tower Lines) | 1 | 2
132kV OHL Support - Tower | 1 | 1.5
132kV OHL Fittings (Tower Lines) | 1 | 2
132kV OHL Conductors (Tower Lines) | 1 | 2

## 221
Asset Category | Access Factor: Type A Criteria - Normal Access ( & Default Value) | Access Factor: Type B Criteria - Constrained Access or Confined Working Space | Access Factor: Type C Criteria - Underground substation
LV Switchgear | 1 | 1.25 | 1.7
HV Transformer (GM) | 1 | 1.25 | 2
HV Switchgear (GM) - Distribution | 1 | 1.25 | 1.7
HV Switchgear (GM) - Primary | 1 | 1.15 | 1.3
EHV Switchgear (GM) | 1 | 1.1 | 1.25
132kV CBs | 1 | 1.1 | 1.2
EHV Transformer | 1 | 1.1 | 1.35
132kV Transformer | 1 | 1.1 | 1.25

## 222
Reference safety cost | Value (GBP)
Lost Time Accident | 9130
Death or Serious Injury to public | 1810495
Death or Serious Injury to staff | 1810495

## 223
Reference safety cost | Value
Disproportion Factor | 6.25

## 224
Asset Register Category | PROBABILITY OF EVENT PER ASSET FAILURE: Lost Time Accident | PROBABILITY OF EVENT PER ASSET FAILURE: Death or Serious Injury to public | PROBABILITY OF EVENT PER ASSET FAILURE: Death or Serious Injury to staff | Reference Safety Cost of Failure*
LV Poles | 0.000816 | 3.264e-05 | 1.632e-05 | 601
6.6/11kV Poles | 0.000272 | 1.088e-05 | 5.44e-06 | 200
20kV Poles | 0.000272 | 1.088e-05 | 5.44e-06 | 200
33kV Pole | 0.000272 | 1.088e-05 | 5.44e-06 | 200
66kV Pole | 0.000272 | 1.088e-05 | 5.44e-06 | 200
33kV Tower | 0.000136 | 5.44e-06 | 2.72e-05 | 377
66kV Tower | 0.000136 | 5.44e-06 | 2.72e-05 | 377
132kV Tower | 0.000136 | 5.44e-06 | 2.72e-05 | 377
33kV Fittings | 0.000544 | 2.176e-05 | 0.0001088 | 1508
66kV Fittings | 0.000544 | 2.176e-05 | 0.0001088 | 1508
132kV Fittings | 0.000544 | 2.176e-05 | 0.0001088 | 1508
33kV OHL (Tower Line) Conductor | 0.000544 | 2.176e-05 | 0.0001088 | 1508
66kV OHL Conductor | 0.000544 | 2.176e-05 | 0.0001088 | 1508
132kV OHL (Tower Line) Conductor | 0.000544 | 2.176e-05 | 0.0001088 | 1508
HV Sub Cable | 7.5e-07 | 7.5e-08 | 7.5e-08 | 2
33kV UG Cable (Non Pressurised) | 7.5e-07 | 7.5e-08 | 7.5e-08 | 2
33kV UG Cable (Oil) | 7.5e-07 | 7.5e-08 | 7.5e-08 | 2
33kV UG Cable (Gas) | 7.5e-07 | 7.5e-08 | 7.5e-08 | 2
66kV UG Cable (Non Pressurised) | 7.5e-07 | 7.5e-08 | 7.5e-08 | 2
66kV UG Cable (Oil) | 7.5e-07 | 7.5e-08 | 7.5e-08 | 2
66kV UG Cable (Gas) | 7.5e-07 | 7.5e-08 | 7.5e-08 | 2
132kV UG Cable (Non Pressurised) | 7.5e-07 | 7.5e-08 | 7.5e-08 | 2
132kV UG Cable (Oil) | 7.5e-07 | 7.5e-08 | 7.5e-08 | 2
132kV UG Cable (Gas) | 7.5e-07 | 7.5e-08 | 7.5e-08 | 2
EHV Sub Cable | 7.5e-07 | 7.5e-08 | 7.5e-08 | 2
132kV Sub Cable | 7.5e-07 | 7.5e-08 | 7.5e-08 | 2
LV Circuit Breaker | 4.916e-05 | 0.00043441 | 0.00037031 | 9109
LV Pillar (ID) | 4.916e-05 | 0.00043441 | 0.00037031 | 9109
LV Pillar (OD at Substation) | 4.916e-05 | 0.00043441 | 0.00037031 | 9109
LV UGB & LV Pillars (OD not at Substation) | 5.193e-05 | 0.00045891 | 0.0003912 | 9622
LV Board (WM) | 4.916e-05 | 0.00043441 | 0.00037031 | 9109
LV Board (X-type Network) (WM) | 4.916e-05 | 0.00043441 | 0.00037031 | 9109
6.6/11kV CB (GM) Primary | 0.00026027 | 0.000115 | 0.0019606 | 23502
6.6/11kV CB (GM) Secondary | 2.6027e-05 | 0.00023 | 0.00019606 | 4823
6.6/11kV Switch (GM) | 2.6027e-05 | 0.00023 | 0.00019606 | 4823
6.6/11kV RMU | 2.6027e-05 | 0.00023 | 0.00019606 | 4823
6.6/11kV X-type RMU | 2.6027e-05 | 0.00023 | 0.00019606 | 4823
20kV CB (GM) Primary | 0.00026027 | 0.000115 | 0.0019606 | 23502
20kV CB (GM) Secondary | 2.6027e-05 | 0.00023 | 0.00019606 | 4823
20kV Switch (GM) | 2.6027e-05 | 0.00023 | 0.00019606 | 4823
20kV RMU | 2.6027e-05 | 0.00023 | 0.00019606 | 4823
33kV CB (Air Insulated Busbars)(ID) (GM) | 0.00026027 | 0.000115 | 0.0019606 | 23502
33kV CB (Air Insulated Busbars)(OD) (GM) | 0.00026027 | 0.000115 | 0.0019606 | 23502
33kV CB (Gas Insulated Busbars)(ID) (GM) | 0.00026027 | 0.000115 | 0.0019606 | 23502
33kV CB (Gas Insulated Busbars)(OD) (GM) | 0.00026027 | 0.000115 | 0.0019606 | 23502
33kV Switch (GM) | 0.00026027 | 0.000115 | 0.0019606 | 23502
33kV RMU | 0.00026027 | 0.000115 | 0.0019606 | 23502
66kV CB (Air Insulated Busbars)(ID) (GM) | 0.00026027 | 0.000115 | 0.0019606 | 23502
66kV CB (Air Insulated Busbars)(OD) (GM) | 0.00026027 | 0.000115 | 0.0019606 | 23502
66kV CB (Gas Insulated Busbars)(ID) (GM) | 0.00026027 | 0.000115 | 0.0019606 | 23502
66kV CB (Gas Insulated Busbars)(OD) (GM) | 0.00026027 | 0.000115 | 0.0019606 | 23502
132kV CB (Air Insulated Busbars)(ID) (GM) | 0.00041644 | 5.75e-05 | 0.003137 | 36171
132kV CB (Air Insulated Busbars)(OD) (GM) | 0.00041644 | 5.75e-05 | 0.003137 | 36171
132kV CB (Gas Insulated Busbars)(ID) (GM) | 0.00041644 | 5.75e-05 | 0.003137 | 36171
132kV CB (Gas Insulated Busbars)(OD) (GM) | 0.00041644 | 5.75e-05 | 0.003137 | 36171
6.6/11kV Transformer (GM) | 2.6027e-05 | 0.00023 | 0.00019606 | 4823
20kV Transformer (GM) | 2.6027e-05 | 0.00023 | 0.00019606 | 4823
33kV Transformer (GM) | 0.00026027 | 0.000115 | 0.0019606 | 23502
Transformador 34kV (GM) | 0.00026027 | 0.000115 | 0.0019606 | 23502
66kV Transformer | 0.00026027 | 0.000115 | 0.0019606 | 23502
132kV Transformer | 0.00041644 | 5.75e-05 | 0.003137 | 36171

## 225
Safety Consequence Factor - Switchgear, Transformers & Overhead Lines | Safety Consequence Factor - Switchgear, Transformers & Overhead Lines | TYPE RISK RATING: Low | TYPE RISK RATING: Medium (Default) | TYPE RISK RATING: High
LOCATION RISK RATING | Low | 0.7 | 0.9 | 1.2
LOCATION RISK RATING | Medium (Default) | 0.9 | 1 | 1.4
LOCATION RISK RATING | High | 1.2 | 1.4 | 1.6

## 226
CABLES | SAFETY CONSEQUENCE FACTOR
Buried | 1
Exposed (e.g. cable structure) | 2

## 227
SAFETY RISK REDUCTION FACTOR
LV UGB with Safety Blanket | 0.5
All other assets – including LV UGB without Safety Blanket, Switchgear, Transformers, Cables & Overhead Lines | 1
Default (no data available) | 1

## 228
Asset Category | Average volume of oil lost per failure (litres) - I | Average volume of oil lost per failure (litres) - D | Average volume of oil lost per failure (litres) - C | Average volume of SF6 lost per failure (kg) - I | Average volume of SF6 lost per failure (kg) - D | Average volume of SF6 lost per failure (kg) - C | Average probability that failure results in a fire - I | Average probability that failure results in a fire - D | Average probability that failure results in a fire - C | Average quantity of waste per failure (t) - I | Average quantity of waste per failure (t) - D | Average quantity of waste per failure (t) - C | Failures as % of All Failures - I | Failures as % of All Failures - D | Failures as % of All Failures - C | Reference Environmental Consequence (GBP)
LV OHL Support | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0005 | 0.5 | 0.5 | 0.5 | 49 | 49 | 2 | 90
HV OHL Support - Poles | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0005 | 0.5 | 0.5 | 0.5 | 49 | 49 | 2 | 90
EHV OHL Support - Poles | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0005 | 0.5 | 0.5 | 0.5 | 49 | 49 | 2 | 90
EHV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.2 | 0.2 | 10 | 45 | 54 | 1 | 54
132kV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.3 | 0.3 | 15 | 45 | 54 | 1 | 81
EHV UG Cable (Oil) | 120 | 120 | 1200 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.8 | 0.8 | 40 | 45 | 54 | 1 | 5885
132kV UG Cable (Oil) | 150 | 150 | 1500 | 0 | 0 | 0 | 0 | 0 | 0.001 | 1.2 | 1.2 | 60 | 45 | 54 | 1 | 7410
LV Switchgear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0002 | 0.005 | 0.01 | 0.1 | 0.25 | 50 | 30 | 20 | 22
LV UGB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0002 | 0.05 | 0.01 | 0.1 | 0.5 | 50 | 30 | 20 | 85
HV Switchgear (GM) - Primary | 10 | 50 | 150 | 0.2 | 0.4 | 0.7 | 0 | 0.0005 | 0.01 | 0.1 | 0.2 | 0.5 | 65 | 30 | 5 | 1547
HV Switchgear (GM) - Distribution | 10 | 50 | 150 | 0.1 | 0.2 | 0.5 | 0 | 0.0005 | 0.01 | 0.1 | 0.2 | 0.5 | 65 | 30 | 5 | 1486
EHV Switchgear (GM) | 25 | 125 | 250 | 0.2 | 0.5 | 1 | 0 | 0.0005 | 0.01 | 0.2 | 0.5 | 2 | 70 | 20 | 10 | 4356
132kV CBs | 50 | 250 | 1000 | 0.5 | 1 | 2 | 0 | 0.0005 | 0.01 | 0.3 | 2 | 10 | 70 | 20 | 10 | 21756
HV Transformer (GM) | 20 | 100 | 300 | 0 | 0 | 0 | 0.0002 | 0.002 | 0.02 | 1 | 2 | 5 | 50 | 40 | 10 | 3809
EHV Transformer | 50 | 250 | 2500 | 0 | 0 | 0 | 0.0002 | 0.002 | 0.02 | 0.2 | 3 | 30 | 50 | 40 | 10 | 17048
132kV Transformer | 100 | 500 | 5000 | 0 | 0 | 0 | 0.0002 | 0.002 | 0.02 | 0.5 | 10 | 100 | 50 | 40 | 10 | 35095
EHV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 4 | 0 | 0 | 100 | 726
132kV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 6 | 0 | 0 | 100 | 1086
Submarine Cables | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 100 | 3600
EHV OHL Support - Towers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 1 | 0 | 0 | 100 | 186
132kV OHL Support - Tower | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 1 | 0 | 0 | 100 | 186
EHV OHL Fittings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0.5 | 0 | 0 | 100 | 96
132kV OHL Fittings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0.5 | 0 | 0 | 100 | 96
EHV OHL Conductor (Tower Lines) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0.5 | 0 | 0 | 100 | 96
132kV OHL Conductor (Tower Lines) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0 | 0 | 0.5 | 0 | 0 | 100 | 96

## 229
Type environment factor | Oil | SF6 | Neither | Default
HV Switchgear (GM) - Primary | 0.97 | 0.05 | 0.02 | 0.97
HV Switchgear (GM) - Distribution | 0.98 | 0.04 | 0.02 | 0.98
EHV Switchgear (GM) | 0.93 | 0.1 | 0.03 | 0.93
132kV CBs | 0.79 | 0.24 | 0.03 | 0.79

## 230
Asset Register Category | Size | Lower | Upper | Bound Description | Size Environmental Factor
6.6/11kV Transformer (GM) |  | 0 | 500 | kVA, Environmental Factor Criteria | 0.6
6.6/11kV Transformer (GM) |  | 500 | 750 | kVA, Environmental Factor Criteria | 1
6.6/11kV Transformer (GM) |  | 750 |  | kVA, Environmental Factor Criteria | 1
20kV Transformer (GM) |  | 0 | 500 | kVA, Environmental Factor Criteria | 0.6
20kV Transformer (GM) |  | 500 | 750 | kVA, Environmental Factor Criteria | 1
20kV Transformer (GM) |  | 750 |  | kVA, Environmental Factor Criteria | 1
33kV Transformer (GM) | 33/20kV | 0 | 10 | MVA, CMR equivalent, Environmental Factor Criteria | 0.7
33kV Transformer (GM) | 33/20kV | 10 | 20 | MVA, CMR equivalent, Environmental Factor Criteria | 1
33kV Transformer (GM) | 33/20kV | 20 |  | MVA, CMR equivalent, Environmental Factor Criteria | 1.6
33kV Transformer (GM) | 33/11 or 6.6kV | 0 | 10 | MVA, CMR equivalent, Environmental Factor Criteria | 0.7
33kV Transformer (GM) | 33/11 or 6.6kV | 10 | 20 | MVA, CMR equivalent, Environmental Factor Criteria | 1
33kV Transformer (GM) | 33/11 or 6.6kV | 20 |  | MVA, CMR equivalent, Environmental Factor Criteria | 1.6
Transformador 34kV (GM) | 33/20kV | 0 | 10 | MVA, CMR equivalent, Environmental Factor Criteria | 0.7
Transformador 34kV (GM) | 33/20kV | 10 | 20 | MVA, CMR equivalent, Environmental Factor Criteria | 1
Transformador 34kV (GM) | 33/20kV | 20 |  | MVA, CMR equivalent, Environmental Factor Criteria | 1.6
Transformador 34kV (GM) | 33/11 or 6.6kV | 0 | 10 | MVA, CMR equivalent, Environmental Factor Criteria | 0.7
Transformador 34kV (GM) | 33/11 or 6.6kV | 10 | 20 | MVA, CMR equivalent, Environmental Factor Criteria | 1
Transformador 34kV (GM) | 33/11 or 6.6kV | 20 |  | MVA, CMR equivalent, Environmental Factor Criteria | 1.6
66kV Transformer (GM) | 66/20kV | 0 | 10 | MVA, CMR equivalent, Environmental Factor Criteria | 0.7
66kV Transformer (GM) |  | 10 | 20 | MVA, CMR equivalent, Environmental Factor Criteria | 1
66kV Transformer (GM) |  | 20 |  | MVA, CMR equivalent, Environmental Factor Criteria | 1.6
66kV Transformer (GM) | 66/11 or 6.6kV | 0 | 10 | MVA, CMR equivalent, Environmental Factor Criteria | 0.7
66kV Transformer (GM) | 66/11 or 6.6kV | 10 | 20 | MVA, CMR equivalent, Environmental Factor Criteria | 1
66kV Transformer (GM) | 66/11 or 6.6kV | 20 |  | MVA, CMR equivalent, Environmental Factor Criteria | 1.6
132kV Transformer (GM) | 132/33kV | 0 | 60 | MVA, Environmental Factor Criteria | 0.8
132kV Transformer (GM) | 132/33kV | 60 |  | MVA, Environmental Factor Criteria | 1
132kV Transformer (GM) | 132/33kV | 0 | 60 | MVA, Environmental Factor Criteria | 0.8
132kV Transformer (GM) | 132/33kV | 60 |  | MVA, Environmental Factor Criteria | 1
66kV Transformer (GM) | 66/33kV |  |  |  | 1.2
66kV Transformer (GM) | 66/11/11kV |  |  |  | 1.2
132kV Transformer (GM) | 132/11/11kV |  |  |  | 0.8
132kV Transformer (GM) | 132/11kV |  |  |  | 0.7
132kV Transformer (GM) | 132/20kV |  |  |  | 0.7
132kV Transformer (GM) | 132/20/20kV |  |  |  | 0.8
132kV Switchgear | 132kV CB (Air Insulated Busbars)(ID)(GM) |  |  |  | 1
132kV Switchgear | 132kV CB (Air Insulated Busbars)(OD)(GM) |  |  |  | 1
132kV Switchgear | 132kV CB (Gas Insulated Busbars)(ID)(GM) |  |  |  | 2.5
132kV Switchgear | 132kV CB (Gas Insulated Busbars)(OD)(GM) |  |  |  | 2.5

## 231
Asset Register Category | Proximity Factor: Not Close to Water Course (>120m) or No Oil | Proximity Factor: Moderately Close to Water Course (between 80m and 120m) | Proximity Factor: Close to Water Course (between 40m and 80m) | Proximity Factor: Very Close to Water Course (<40m) | Bunding Factor: Bunded | Bunding Factor: Not bunded
EHV UG Cable (Oil) | 0.8 | 1 | 1.5 | 2.5 | 0.5 | 1
132kV UG Cable (Oil) | 0.8 | 1 | 1.5 | 2.5 | 0.5 | 1
HV Switchgear (GM) - Primary | 0.8 | 1 | 1.5 | 2.5 | 0.5 | 1
HV Switchgear (GM) - Distribution | 0.8 | 1 | 1.5 | 2.5 | 0.5 | 1
EHV Switchgear (GM) | 0.8 | 1 | 1.5 | 2.5 | 0.5 | 1
132kV CBs | 0.8 | 1 | 1.5 | 2.5 | 0.5 | 1
HV Transformer (GM) | 0.8 | 1 | 1.5 | 2.5 | 0.5 | 1
EHV Transformer | 0.8 | 1 | 1.5 | 2.5 | 0.5 | 1
132kV Transformer | 0.8 | 1 | 1.5 | 2.5 | 0.5 | 1

## 232
Parameter | GBP (at 2020/21 prices)
Cost of CML | 0.45
Cost of CI | 18.55

## 233
Asset Category | Reference Number of Connected Customers | Proportion of connected customers restored through immediate (< 3min) switching (%) | Proportion of customers restored After manual switching (%) | Manual switching time (hours) | Typical repair time (hours) | Proportion of failures that result in interruption to supply (%) | Reference Network Performance Cost (GBP)
LV OHL Support | 80 | 0 | 0 | 1 | 5 | 10 | 542
HV OHL Support - Poles | 800 | 60 | 94 | 0.5 | 4 | 10 | 1930
HV Transformer (GM) | 200 | 0 | 85 | 0.5 | 4 | 60 | 4343
HV Switchgear (GM) - Distribution | 800 | 60 | 94 | 0.5 | 4 | 60 | 11580
HV Switchgear (GM) - Primary | 1000 | 60 | 94 | 0.5 | 4 | 60 | 40530
LV Circuit Breaker | 200 | 0 | 85 | 1 | 7 | 100 | 11085
LV Pillar | 200 | 25 | 89 | 1 | 7 | 100 | 8243
LV UGB | 80 | 25 | 89 | 1 | 7 | 100 | 2748
LV Board (WM) | 200 | 25 | 89 | 1 | 7 | 100 | 8243
HV Sub Cable | 800 | 40 | 60 | 2 | 18 | 100 | 190344

## 234
Lower | Upper | Bound Description | No. of Customers to be used in the derivation of Customer Factor
0 | 50 | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) Higher Bound | 1 x actual number of customers fed by the asset
50 | 100 | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) Higher Bound | 25 x actual number of customers fed by the asset
100 | 500 | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) Higher Bound | 100 x actual number of customers fed by the asset
500 | 1000 | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) Higher Bound | 250 x actual number of customers fed by the asset
1000 | 2000 | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) Higher Bound | 500 x actual number of customers fed by the asset
2000 |  | Maximum Demand on Asset / Total Number of Customers fed by the Asset (kVA per Customer) Higher Bound | 1000 x actual number of customers fed by the asset

## 235
Asset Category | Maximum Demand Used To Derive Reference Cost (MVA) | Load at Risk (MVA) as % of Maximum Demand - During T1 period (%) | Load at Risk (MVA) as % of Maximum Demand - During T2 period (%) | Load at Risk (MVA) as % of Maximum Demand - During T3 period (%) | Time (hours) - T1 | Time (hours) - T2 | Time (hours) - T3 | Probability of a coincident fault per hr (%) | Proportion of failures that result in an unplanned outage (%) | Reference Cost For Assets In Secure Networks (GBP)
33kV Pole | 12 | 100 | 100 | 80 | 0 | 3 | 5 | 0.05 | 10 | 92
66kV Pole | 24 | 100 | 100 | 80 | 0 | 3 | 5 | 0.05 | 10 | 183
33kV Tower | 12 | 100 | 100 | 80 | 0 | 3 | 24 | 0.05 | 20 | 580
66kV Tower | 24 | 100 | 100 | 80 | 0 | 3 | 36 | 0.05 | 20 | 1663
132kV Tower | 60 | 100 | 100 | 80 | 0 | 3 | 36 | 0.05 | 20 | 4157
33kV Fittings | 12 | 100 | 100 | 80 | 0 | 3 | 9 | 0.05 | 20 | 267
66kV Fittings | 24 | 100 | 100 | 80 | 0 | 3 | 9 | 0.05 | 20 | 533
132kV Fittings | 60 | 100 | 100 | 80 | 0 | 3 | 9 | 0.05 | 20 | 1333
33kV OHL (Tower Line) Conductor | 12 | 100 | 100 | 80 | 0 | 3 | 9 | 0.05 | 100 | 1333
66kV OHL Conductor | 24 | 100 | 100 | 80 | 0 | 3 | 9 | 0.05 | 100 | 2667
132kV OHL (Tower Line) Conductor | 60 | 100 | 100 | 80 | 0 | 3 | 9 | 0.05 | 100 | 6667
33kV UG Cable (Non Pressurised) | 12 | 100 | 100 | 80 | 0 | 3 | 30 | 0.05 | 100 | 3530
33kV UG Cable (Oil) | 12 | 100 | 100 | 80 | 0 | 3 | 30 | 0.05 | 0.1 | 4
33kV UG Cable (Gas) | 12 | 100 | 100 | 80 | 0 | 3 | 30 | 0.05 | 1 | 35
66kV UG Cable (Non Pressurised) | 24 | 100 | 100 | 80 | 0 | 3 | 30 | 0.05 | 100 | 7059
66kV UG Cable (Oil) | 24 | 100 | 100 | 80 | 0 | 3 | 30 | 0.05 | 0.1 | 7
66kV UG Cable (Gas) | 24 | 100 | 100 | 80 | 0 | 3 | 30 | 0.05 | 1 | 71
132kV UG Cable (Non Pressurised) | 60 | 100 | 100 | 80 | 0 | 3 | 30 | 0.05 | 100 | 17648
132kV UG Cable (Oil) | 60 | 100 | 100 | 80 | 0 | 3 | 30 | 0.05 | 0.1 | 18
132kV UG Cable (Gas) | 60 | 100 | 100 | 80 | 0 | 3 | 30 | 0.05 | 1 | 176
EHV Sub Cable | 12 | 100 | 100 | 80 | 0 | 3 | 30 | 0.05 | 100 | 3530
132kV Sub Cable | 60 | 100 | 100 | 80 | 0 | 3 | 30 | 0.05 | 100 | 17648
33kV CB (Air Insulated Busbars)(ID) (GM) | 30 | 100 | 100 | 80 | 0 | 2 | 200 | 0.05 | 55 | 29120
33kV CB (Air Insulated Busbars)(OD) (GM) | 30 | 100 | 100 | 80 | 0 | 2 | 100 | 0.05 | 55 | 14740
33kV CB (Gas Insulated Busbars)(ID) (GM) | 30 | 100 | 100 | 80 | 0 | 2 | 200 | 0.05 | 55 | 29120
33kV CB (Gas Insulated Busbars)(OD) (GM) | 30 | 100 | 100 | 80 | 0 | 2 | 100 | 0.05 | 55 | 14740
33kV Switch (GM) | 30 | 100 | 100 | 80 | 0 | 2 | 100 | 0.05 | 55 | 14740
33kV RMU | 30 | 100 | 100 | 80 | 0 | 2 | 100 | 0.05 | 55 | 14740
66kV CB (Air Insulated Busbars)(ID) (GM) | 30 | 100 | 100 | 80 | 0 | 2 | 200 | 0.05 | 55 | 29120
66kV CB (Air Insulated Busbars)(OD) (GM) | 30 | 100 | 100 | 80 | 0 | 2 | 100 | 0.05 | 55 | 14740
66kV CB (Gas Insulated Busbars)(ID) (GM) | 30 | 100 | 100 | 80 | 0 | 2 | 200 | 0.05 | 55 | 29120
66kV CB (Gas Insulated Busbars)(OD) (GM) | 30 | 100 | 100 | 80 | 0 | 2 | 100 | 0.05 | 55 | 14740
132kV CB (Air Insulated Busbars)(ID) (GM) | 80 | 100 | 100 | 80 | 0 | 1 | 400 | 0.05 | 55 | 153867
132kV CB (Air Insulated Busbars)(OD) (GM) | 80 | 100 | 100 | 80 | 0 | 1 | 100 | 0.05 | 55 | 38826
132kV CB (Gas Insulated Busbars)(ID) (GM) | 80 | 100 | 100 | 80 | 0 | 1 | 400 | 0.05 | 55 | 153867
132kV CB (Gas Insulated Busbars)(OD) (GM) | 80 | 100 | 100 | 80 | 0 | 1 | 100 | 0.05 | 55 | 38826
33kV Transformer (GM) | 15 | 100 | 100 | 80 | 0 | 2 | 400 | 0.05 | 55 | 28940
Transformador 34kV (GM) | 15 | 100 | 100 | 80 | 0 | 2 | 400 | 0.05 | 55 | 28940
66kV Transformer | 15 | 100 | 100 | 80 | 0 | 2 | 400 | 0.05 | 55 | 28940
132kV Transformer | 60 | 100 | 100 | 80 | 0 | 1 | 800 | 0.05 | 55 | 230441

## 236
Asset Register Category | C1: Typical COF Weightings for Each Criticality Index Band (£ at 20/21 prices) | C2: Typical COF Weightings for Each Criticality Index Band (£ at 20/21 prices) | C3: Typical COF Weightings for Each Criticality Index Band (£ at 20/21 prices) | C4: Typical COF Weightings for Each Criticality Index Band (£ at 20/21 prices)
LV Poles | 1798.78 | 2569.68 | 3854.53 | 6424.21
LV Circuit Breaker | 16999.67 | 24285.24 | 36427.86 | 60713.1
LV Pillar (ID) | 16129.41 | 23042.02 | 34563.02 | 57605.04
LV Pillar (OD at Substation) | 16480.36 | 23543.37 | 35315.05 | 58858.42
LV Pillar (OD not at a Substation) | 14921.01 | 21315.73 | 31973.6 | 53289.33
LV Board (WM) | 17644.46 | 25206.37 | 37809.55 | 63015.92
LV UGB | 11118.48 | 15883.55 | 23825.32 | 39708.86
LV Board (X-type Network) (WM) | 18632.02 | 26617.17 | 39925.75 | 66542.92
6.6/11kV Poles | 2893.28 | 4133.25 | 6199.88 | 10333.13
20kV Poles | 3160.82 | 4515.45 | 6773.18 | 11288.63
HV Sub Cable | 263159.22 | 375941.74 | 563912.61 | 939854.35
6.6/11kV CB (GM) Primary | 51215.17 | 73164.53 | 109746.8 | 182911.33
6.6/11kV CB (GM) Secondary | 17393.48 | 24847.83 | 37271.74 | 62119.57
6.6/11kV Switch (GM) | 16209.05 | 23155.78 | 34733.67 | 57889.45
6.6/11kV RMU | 19409.55 | 27727.93 | 41591.89 | 69319.82
6.6/11kV X-type RMU | 21842.3 | 31203.28 | 46804.92 | 78008.2
20kV CB (GM) Primary | 52557.6 | 75082.28 | 112623.43 | 187705.71
20kV CB (GM) Secondary | 17571.91 | 25102.73 | 37654.09 | 62756.82
20kV Switch (GM) | 16795.26 | 23993.23 | 35989.84 | 59983.07
20kV RMU | 19538.7 | 27912.43 | 41868.64 | 69781.07
6.6/11kV Transformer (GM) | 15589.91 | 22271.3 | 33406.95 | 55678.25
20kV Transformer (GM) | 16491.93 | 23559.9 | 35339.85 | 58899.75
33kV Pole | 1993.15 | 2847.36 | 4271.04 | 7118.4
66kV Pole | 2933.75 | 4191.07 | 6286.61 | 10477.68
33kV OHL (Tower Line) Conductor | 14511.55 | 20730.79 | 31096.18 | 51826.97
33kV Tower | 5525.07 | 7892.96 | 11839.43 | 19732.39
33kV Fittings | 1468.88 | 2098.4 | 3147.6 | 5246
66kV OHL (Tower Line) Conductor | 19509.99 | 27871.41 | 41807.12 | 69678.54
66kV Tower | 10410.78 | 14872.54 | 22308.81 | 37181.36
66kV Fittings | 1700.64 | 2429.48 | 3644.22 | 6073.71
33kV UG Cable (Non Pressurised) | 25130.98 | 35901.4 | 53852.1 | 89753.51
33kV UG Cable (Oil) | 4213.41 | 6019.15 | 9028.73 | 15047.89
33kV UG Cable (Gas) | 285.12 | 407.31 | 610.97 | 1018.28
66kV UG Cable (Non Pressurised) | 50265.64 | 71808.06 | 107712.09 | 179520.15
66kV UG Cable (Oil) | 4223.24 | 6033.21 | 9049.81 | 15083.02
66kV UG Cable (Gas) | 451.48 | 644.97 | 967.45 | 1612.42
EHV Sub Cable | 204717.38 | 292453.4 | 438680.09 | 731133.49
33kV CB (Air Insulated Busbars)(ID)(GM) | 50043.29 | 71490.41 | 107235.62 | 178726.04
33kV CB (Air Insulated Busbars)(OD)(GM) | 42326.71 | 60466.73 | 90700.1 | 151166.84
33kV CB (Gas Insulated Busbars)(ID)(GM) | 55272.53 | 78960.76 | 118441.15 | 197401.91
33kV CB (Gas Insulated Busbars)(OD)(GM) | 45206.48 | 64580.68 | 96871.03 | 161451.71
33kV Switch (GM) | 36997.86 | 52854.08 | 79281.13 | 132135.21
33kV RMU | 47561 | 67944.28 | 101916.43 | 169860.71
66kV CB (Air Insulated Busbars)(ID)(GM) | 60135.01 | 85907.16 | 128860.75 | 214767.91
66kV CB (Air Insulated Busbars)(OD)(GM) | 62194.5 | 88849.28 | 133273.93 | 222123.21
66kV CB (Gas Insulated Busbars)(ID)(GM) | 76407.14 | 109153.06 | 163729.6 | 272882.66
66kV CB (Gas Insulated Busbars)(OD)(GM) | 66341.09 | 94772.98 | 142159.48 | 236932.46
33kV Transformer (GM) | 110031.29 | 157187.56 | 235781.34 | 392968.9
Transformador 34kV (GM) | 110031.29 | 157187.56 | 235781.34 | 392968.9
66kV Transformer (GM) | 142999.65 | 204285.21 | 306427.82 | 510713.03
132kV OHL (Tower Line) Conductor | 20075.71 | 28679.59 | 43019.39 | 71698.98
132kV Tower | 13540.32 | 19343.32 | 29014.98 | 48358.3
132kV Fittings | 2396.27 | 3423.24 | 5134.86 | 8558.1
132kV UG Cable (Non Pressurised) | 89586.02 | 127980.03 | 191970.04 | 319950.07
132kV UG Cable (Oil) | 5308.32 | 7583.32 | 11374.98 | 18958.29
132kV UG Cable (Gas) | 742.22 | 1060.31 | 1590.47 | 2650.78
132kV Sub Cable | 351254.41 | 501792.02 | 752688.03 | 1254480.05
132kV CB (Air Insulated Busbars)(ID)(GM) | 205020.01 | 292885.73 | 439328.6 | 732214.33
132kV CB (Air Insulated Busbars)(OD)(GM) | 94453.62 | 134933.74 | 202400.61 | 337334.36
132kV CB (Gas Insulated Busbars)(ID)(GM) | 266480.05 | 380685.78 | 571028.67 | 951714.46
132kV CB (Gas Insulated Busbars)(OD)(GM) | 185951.6 | 265645.14 | 398467.71 | 664112.86
132kV Transformer (GM) | 395305.03 | 564721.47 | 847082.21 | 1411803.68

## 237
Asset Register Category | H1: Typical In-Year POF Weightings for Each Health Index Band | H2: Typical In-Year POF Weightings for Each Health Index Band | H3: Typical In-Year POF Weightings for Each Health Index Band | H4: Typical In-Year POF Weightings for Each Health Index Band | H5: Typical In-Year POF Weightings for Each Health Index Band
LV Poles | 0.008123 | 0.009326 | 0.021383 | 0.03463 | 0.061186
LV Circuit Breaker | 0.001169 | 0.001342 | 0.003076 | 0.004982 | 0.008802
LV Pillar (ID) | 0.001311 | 0.001505 | 0.003451 | 0.005589 | 0.009876
LV Pillar (OD at Substation) | 0.001311 | 0.001505 | 0.003451 | 0.005589 | 0.009876
LV Pillar (OD not at a Substation) | 0.001311 | 0.001505 | 0.003451 | 0.005589 | 0.009876
LV Board (WM) | 0.001967 | 0.002258 | 0.005177 | 0.008384 | 0.014813
LV UGB | 0.002195 | 0.00252 | 0.005777 | 0.009356 | 0.016531
LV Board (X-type Network) (WM) | 0.001967 | 0.002258 | 0.005177 | 0.008384 | 0.014813
6.6/11kV Poles | 0.008123 | 0.009326 | 0.021383 | 0.03463 | 0.061186
20kV Poles | 0.008123 | 0.009326 | 0.021383 | 0.03463 | 0.061186
HV Sub Cable | 0.005757 | 0.00661 | 0.015156 | 0.024545 | 0.043367
6.6/11kV CB (GM) Primary | 0.001482 | 0.001702 | 0.003901 | 0.006318 | 0.011164
6.6/11kV CB (GM) Secondary | 0.00191 | 0.002192 | 0.005027 | 0.008141 | 0.014384
6.6/11kV Switch (GM) | 0.00191 | 0.002192 | 0.005027 | 0.008141 | 0.014384
6.6/11kV RMU | 0.00191 | 0.002192 | 0.005027 | 0.008141 | 0.014384
6.6/11kV X-type RMU | 0.00191 | 0.002192 | 0.005027 | 0.008141 | 0.014384
20kV CB (GM) Primary | 0.001482 | 0.001702 | 0.003901 | 0.006318 | 0.011164
20kV CB (GM) Secondary | 0.00191 | 0.002192 | 0.005027 | 0.008141 | 0.014384
20kV Switch (GM) | 0.00191 | 0.002192 | 0.005027 | 0.008141 | 0.014384
20kV RMU | 0.00191 | 0.002192 | 0.005027 | 0.008141 | 0.014384
6.6/11kV Transformer (GM) | 0.002223 | 0.002552 | 0.005852 | 0.009478 | 0.016746
20kV Transformer (GM) | 0.002223 | 0.002552 | 0.005852 | 0.009478 | 0.016746
33kV Pole | 0.008123 | 0.009326 | 0.021383 | 0.03463 | 0.061186
66kV Pole | 0.008123 | 0.009326 | 0.021383 | 0.03463 | 0.061186
33kV OHL (Tower Line) Conductor | 0.00228 | 0.002618 | 0.006002 | 0.009721 | 0.017175
33kV Tower | 0.015533 | 0.017834 | 0.04089 | 0.066222 | 0.117
33kV Fittings | 0.002736 | 0.003141 | 0.007203 | 0.011665 | 0.02061
66kV OHL (Tower Line) Conductor | 0.00228 | 0.002618 | 0.006002 | 0.009721 | 0.017175
66kV Tower | 0.015533 | 0.017834 | 0.04089 | 0.066222 | 0.117
66kV Fittings | 0.002736 | 0.003141 | 0.007203 | 0.011665 | 0.02061
33kV UG Cable (Non Pressurised) | 0.018753 | 0.021532 | 0.049368 | 0.079952 | 0.14126
33kV UG Cable (Oil) | 0.59691 | 0.68536 | 1.5714 | 2.5449 | 4.4964
33kV UG Cable (Gas) | 1.2835 | 1.4737 | 3.3789 | 5.4722 | 9.6686
66kV UG Cable (Non Pressurised) | 0.018753 | 0.021532 | 0.049368 | 0.079952 | 0.14126
66kV UG Cable (Oil) | 0.59691 | 0.68536 | 1.5714 | 2.5449 | 4.4964
66kV UG Cable (Gas) | 1.2835 | 1.4737 | 3.3789 | 5.4722 | 9.6686
EHV Sub Cable | 0.005757 | 0.00661 | 0.015156 | 0.024545 | 0.043367
33kV CB (Air Insulated Busbars)(ID)(GM) | 0.006356 | 0.007297 | 0.016731 | 0.027096 | 0.047875
33kV CB (Air Insulated Busbars)(OD)(GM) | 0.006356 | 0.007297 | 0.016731 | 0.027096 | 0.047875
33kV CB (Gas Insulated Busbars)(ID)(GM) | 0.006356 | 0.007297 | 0.016731 | 0.027096 | 0.047875
33kV CB (Gas Insulated Busbars)(OD)(GM) | 0.006356 | 0.007297 | 0.016731 | 0.027096 | 0.047875
33kV Switch (GM) | 0.006356 | 0.007297 | 0.016731 | 0.027096 | 0.047875
33kV RMU | 0.006356 | 0.007297 | 0.016731 | 0.027096 | 0.047875
66kV CB (Air Insulated Busbars)(ID)(GM) | 0.014592 | 0.016754 | 0.038414 | 0.062212 | 0.10992
66kV CB (Air Insulated Busbars)(OD)(GM) | 0.014592 | 0.016754 | 0.038414 | 0.062212 | 0.10992
66kV CB (Gas Insulated Busbars)(ID)(GM) | 0.014592 | 0.016754 | 0.038414 | 0.062212 | 0.10992
66kV CB (Gas Insulated Busbars)(OD)(GM) | 0.014592 | 0.016754 | 0.038414 | 0.062212 | 0.10992
33kV Transformer (GM) | 0.012939 | 0.014856 | 0.034062 | 0.055165 | 0.097468
Transformador 34kV (GM) | 0.012939 | 0.014856 | 0.034062 | 0.055165 | 0.097468
66kV Transformer (GM) | 0.012939 | 0.014856 | 0.034062 | 0.055165 | 0.097468
132kV OHL (Tower Line) Conductor | 0.00228 | 0.002618 | 0.006002 | 0.009721 | 0.017175
132kV Tower | 0.015533 | 0.017834 | 0.04089 | 0.066222 | 0.117
132kV Fittings | 0.002736 | 0.003141 | 0.007203 | 0.011665 | 0.02061
132kV UG Cable (Non Pressurised) | 0.018753 | 0.021532 | 0.049368 | 0.079952 | 0.14126
132kV UG Cable (Oil) | 0.59691 | 0.68536 | 1.5714 | 2.5449 | 4.4964
132kV UG Cable (Gas) | 1.2835 | 1.4737 | 3.3789 | 5.4722 | 9.6686
132kV Sub Cable | 0.005757 | 0.00661 | 0.015156 | 0.024545 | 0.043367
132kV CB (Air Insulated Busbars)(ID)(GM) | 0.012284 | 0.014104 | 0.032337 | 0.05237 | 0.09253
132kV CB (Air Insulated Busbars)(OD)(GM) | 0.012284 | 0.014104 | 0.032337 | 0.05237 | 0.09253
132kV CB (Gas Insulated Busbars)(ID)(GM) | 0.012284 | 0.014104 | 0.032337 | 0.05237 | 0.09253
132kV CB (Gas Insulated Busbars)(OD)(GM) | 0.012284 | 0.014104 | 0.032337 | 0.05237 | 0.09253
132kV Transformer (GM) | 0.012939 | 0.014856 | 0.034062 | 0.055165 | 0.097468

## 238
Asset Register Category | Criticality Index Band | H1: In Year Monetised Risk Weighting (£ at 2020/21 prices) For Each Health Index Band | H2: In Year Monetised Risk Weighting (£ at 2020/21 prices) For Each Health Index Band | H3: In Year Monetised Risk Weighting (£ at 2020/21 prices) For Each Health Index Band | H4: In Year Monetised Risk Weighting (£ at 2020/21 prices) For Each Health Index Band | H5: In Year Monetised Risk Weighting (£ at 2020/21 prices) For Each Health Index Band
LV Poles | C1 | 15 | 17 | 38 | 62 | 110
LV Poles | C2 | 21 | 24 | 55 | 89 | 157
LV Poles | C3 | 31 | 36 | 82 | 133 | 236
LV Poles | C4 | 52 | 60 | 137 | 222 | 393
LV Circuit Breaker | C1 | 20 | 23 | 52 | 85 | 150
LV Circuit Breaker | C2 | 28 | 33 | 75 | 121 | 214
LV Circuit Breaker | C3 | 43 | 49 | 112 | 181 | 321
LV Circuit Breaker | C4 | 71 | 81 | 187 | 302 | 534
| C1 | 21 | 24 | 56 | 90 | 159
LV Pillar (ID) | C2 | 30 | 35 | 80 | 129 | 228
LV Pillar (ID) | C3 | 45 | 52 | 119 | 193 | 341
LV Pillar (ID) | C4 | 76 | 87 | 199 | 322 | 569
LV Pillar (OD at Substation) | C1 | 22 | 25 | 57 | 92 | 163
LV Pillar (OD at Substation) | C2 | 31 | 35 | 81 | 132 | 233
LV Pillar (OD at Substation) | C3 | 46 | 53 | 122 | 197 | 349
LV Pillar (OD at Substation) | C4 | 77 | 89 | 203 | 329 | 581
LV Pillar (OD not at a Substation) | C1 | 20 | 22 | 51 | 83 | 147
LV Pillar (OD not at a Substation) | C2 | 28 | 32 | 74 | 119 | 211
LV Pillar (OD not at a Substation) | C3 | 42 | 48 | 110 | 179 | 316
LV Pillar (OD not at a Substation) | C4 | 70 | 80 | 184 | 298 | 526
LV Board (WM) | C1 | 35 | 40 | 91 | 148 | 261
LV Board (WM) | C2 | 50 | 57 | 130 | 211 | 373
LV Board (WM) | C3 | 74 | 85 | 196 | 317 | 560
LV Board (WM) | C4 | 124 | 142 | 326 | 528 | 933
LV UGB | C1 | 24 | 28 | 64 | 104 | 184
LV UGB | C2 | 35 | 40 | 92 | 149 | 263
LV UGB | C3 | 52 | 60 | 138 | 223 | 394
LV UGB | C4 | 87 | 100 | 229 | 372 | 656
LV Board (X-type Network) (WM) | C1 | 37 | 42 | 96 | 156 | 276
LV Board (X-type Network) (WM) | C2 | 52 | 60 | 138 | 223 | 394
LV Board (X-type Network) (WM) | C3 | 79 | 90 | 207 | 335 | 591
LV Board (X-type Network) (WM) | C4 | 131 | 150 | 344 | 558 | 986
6.6/11kV Poles | C1 | 24 | 27 | 62 | 100 | 177
6.6/11kV Poles | C2 | 34 | 39 | 88 | 143 | 253
6.6/11kV Poles | C3 | 50 | 58 | 133 | 215 | 379
6.6/11kV Poles | C4 | 84 | 96 | 221 | 358 | 632
20kV Poles | C1 | 26 | 29 | 68 | 109 | 193
20kV Poles | C2 | 37 | 42 | 97 | 156 | 276
20kV Poles | C3 | 55 | 63 | 145 | 235 | 414
20kV Poles | C4 | 92 | 105 | 241 | 391 | 691
HV Sub Cable | C1 | 1515 | 1739 | 3988 | 6459 | 11412
HV Sub Cable | C2 | 2164 | 2485 | 5698 | 9227 | 16303
HV Sub Cable | C3 | 3246 | 3727 | 8547 | 13841 | 24455
HV Sub Cable | C4 | 5411 | 6212 | 14244 | 23069 | 40759
6.6/11kV CB (GM) Primary | C1 | 76 | 87 | 200 | 324 | 572
6.6/11kV CB (GM) Primary | C2 | 108 | 125 | 285 | 462 | 817
6.6/11kV CB (GM) Primary | C3 | 163 | 187 | 428 | 693 | 1225
6.6/11kV CB (GM) Primary | C4 | 271 | 311 | 714 | 1156 | 2042
6.6/11kV CB (GM) Secondary | C1 | 33 | 38 | 87 | 142 | 250
6.6/11kV CB (GM) Secondary | C2 | 47 | 54 | 125 | 202 | 357
6.6/11kV CB (GM) Secondary | C3 | 71 | 82 | 187 | 303 | 536
6.6/11kV CB (GM) Secondary | C4 | 119 | 136 | 312 | 506 | 894
6.6/11kV Switch (GM) | C1 | 31 | 36 | 81 | 132 | 233
6.6/11kV Switch (GM) | C2 | 44 | 51 | 116 | 189 | 333
6.6/11kV Switch (GM) | C3 | 66 | 76 | 175 | 283 | 500
6.6/11kV Switch (GM) | C4 | 111 | 127 | 291 | 471 | 833
6.6/11kV RMU | C1 | 37 | 43 | 98 | 158 | 279
6.6/11kV RMU | C2 | 53 | 61 | 139 | 226 | 399
6.6/11kV RMU | C3 | 79 | 91 | 209 | 339 | 598
6.6/11kV RMU | C4 | 132 | 152 | 348 | 564 | 997
6.6/11kV X-type RMU | C1 | 42 | 48 | 110 | 178 | 314
6.6/11kV X-type RMU | C2 | 60 | 68 | 157 | 254 | 449
6.6/11kV X-type RMU | C3 | 89 | 103 | 235 | 381 | 673
6.6/11kV X-type RMU | C4 | 149 | 171 | 392 | 635 | 1122
20kV CB (GM) Primary | C1 | 78 | 89 | 205 | 332 | 587
20kV CB (GM) Primary | C2 | 111 | 128 | 293 | 474 | 838
20kV CB (GM) Primary | C3 | 167 | 192 | 439 | 712 | 1257
20kV CB (GM) Primary | C4 | 278 | 319 | 732 | 1186 | 2096
20kV CB (GM) Secondary | C1 | 34 | 39 | 88 | 143 | 253
20kV CB (GM) Secondary | C2 | 48 | 55 | 126 | 204 | 361
20kV CB (GM) Secondary | C3 | 72 | 83 | 189 | 307 | 542
20kV CB (GM) Secondary | C4 | 120 | 138 | 315 | 511 | 903
20kV Switch (GM) | C1 | 32 | 37 | 84 | 137 | 242
20kV Switch (GM) | C2 | 46 | 53 | 121 | 195 | 345
20kV Switch (GM) | C3 | 69 | 79 | 181 | 293 | 518
20kV Switch (GM) | C4 | 115 | 131 | 302 | 488 | 863
20kV RMU | C1 | 37 | 43 | 98 | 159 | 281
20kV RMU | C2 | 53 | 61 | 140 | 227 | 401
20kV RMU | C3 | 80 | 92 | 210 | 341 | 602
20kV RMU | C4 | 133 | 153 | 351 | 568 | 1004
6.6/11kV Transformer (GM) | C1 | 35 | 40 | 91 | 148 | 261
6.6/11kV Transformer (GM) | C2 | 50 | 57 | 130 | 211 | 373
6.6/11kV Transformer (GM) | C3 | 74 | 85 | 195 | 317 | 559
6.6/11kV Transformer (GM) | C4 | 124 | 142 | 326 | 528 | 932
20kV Transformer (GM) | C1 | 37 | 42 | 97 | 156 | 276
20kV Transformer (GM) | C2 | 52 | 60 | 138 | 223 | 395
20kV Transformer (GM) | C3 | 79 | 90 | 207 | 335 | 592
20kV Transformer (GM) | C4 | 131 | 150 | 345 | 558 | 986
33kV Pole | C1 | 16 | 19 | 43 | 69 | 122
33kV Pole | C2 | 23 | 27 | 61 | 99 | 174
33kV Pole | C3 | 35 | 40 | 91 | 148 | 261
33kV Pole | C4 | 58 | 66 | 152 | 247 | 436
66kV Pole | C1 | 24 | 27 | 63 | 102 | 180
66kV Pole | C2 | 34 | 39 | 90 | 145 | 256
66kV Pole | C3 | 51 | 59 | 134 | 218 | 385
66kV Pole | C4 | 85 | 98 | 224 | 363 | 641
33kV OHL (Tower Line) Conductor | C1 | 33 | 38 | 87 | 141 | 249
33kV OHL (Tower Line) Conductor | C2 | 47 | 54 | 124 | 202 | 356
33kV OHL (Tower Line) Conductor | C3 | 71 | 81 | 187 | 302 | 534
33kV OHL (Tower Line) Conductor | C4 | 118 | 136 | 311 | 504 | 890
33kV Tower | C1 | 86 | 99 | 226 | 366 | 646
33kV Tower | C2 | 123 | 141 | 323 | 523 | 924
33kV Tower | C3 | 184 | 211 | 484 | 784 | 1385
33kV Tower | C4 | 307 | 352 | 807 | 1307 | 2309
33kV Fittings | C1 | 4 | 5 | 11 | 17 | 30
33kV Fittings | C2 | 6 | 7 | 15 | 24 | 43
33kV Fittings | C3 | 9 | 10 | 23 | 37 | 65
33kV Fittings | C4 | 14 | 16 | 38 | 61 | 108
66kV OHL (Tower Line) Conductor | C1 | 44 | 51 | 117 | 190 | 335
66kV OHL (Tower Line) Conductor | C2 | 64 | 73 | 167 | 271 | 479
66kV OHL (Tower Line) Conductor | C3 | 95 | 109 | 251 | 406 | 718
66kV OHL (Tower Line) Conductor | C4 | 159 | 182 | 418 | 677 | 1197
66kV Tower | C1 | 162 | 186 | 426 | 689 | 1218
66kV Tower | C2 | 231 | 265 | 608 | 985 | 1740
66kV Tower | C3 | 347 | 398 | 912 | 1477 | 2610
66kV Tower | C4 | 578 | 663 | 1520 | 2462 | 4350
66kV Fittings | C1 | 5 | 5 | 12 | 20 | 35
66kV Fittings | C2 | 7 | 8 | 17 | 28 | 50
66kV Fittings | C3 | 10 | 11 | 26 | 43 | 75
66kV Fittings | C4 | 17 | 19 | 44 | 71 | 125
33kV UG Cable (Non Pressurised) | C1 | 471 | 541 | 1241 | 2009 | 3550
33kV UG Cable (Non Pressurised) | C2 | 673 | 773 | 1772 | 2870 | 5072
33kV UG Cable (Non Pressurised) | C3 | 1010 | 1160 | 2659 | 4306 | 7607
33kV UG Cable (Non Pressurised) | C4 | 1683 | 1933 | 4431 | 7176 | 12679
33kV UG Cable (Oil) | C1 | 2515 | 2888 | 6621 | 10723 | 18945
33kV UG Cable (Oil) | C2 | 3593 | 4125 | 9458 | 15318 | 27065
33kV UG Cable (Oil) | C3 | 5389 | 6188 | 14188 | 22977 | 40597
33kV UG Cable (Oil) | C4 | 8982 | 10313 | 23646 | 38295 | 67661
33kV UG Cable (Gas) | C1 | 366 | 420 | 963 | 1560 | 2757
33kV UG Cable (Gas) | C2 | 523 | 600 | 1376 | 2229 | 3938
33kV UG Cable (Gas) | C3 | 784 | 900 | 2064 | 3343 | 5907
33kV UG Cable (Gas) | C4 | 1307 | 1501 | 3441 | 5572 | 9845
66kV UG Cable (Non Pressurised) | C1 | 943 | 1082 | 2482 | 4019 | 7101
66kV UG Cable (Non Pressurised) | C2 | 1347 | 1546 | 3545 | 5741 | 10144
66kV UG Cable (Non Pressurised) | C3 | 2020 | 2319 | 5318 | 8612 | 15216
66kV UG Cable (Non Pressurised) | C4 | 3367 | 3865 | 8863 | 14353 | 25360
66kV UG Cable (Oil) | C1 | 2521 | 2894 | 6636 | 10748 | 18989
66kV UG Cable (Oil) | C2 | 3601 | 4135 | 9480 | 15354 | 27128
66kV UG Cable (Oil) | C3 | 5402 | 6202 | 14221 | 23030 | 40692
66kV UG Cable (Oil) | C4 | 9003 | 10337 | 23701 | 38384 | 67819
66kV UG Cable (Gas) | C1 | 579 | 665 | 1526 | 2471 | 4365
66kV UG Cable (Gas) | C2 | 828 | 951 | 2179 | 3529 | 6236
66kV UG Cable (Gas) | C3 | 1242 | 1426 | 3269 | 5294 | 9354
66kV UG Cable (Gas) | C4 | 2070 | 2376 | 5448 | 8824 | 15590
EHV Sub Cable | C1 | 1179 | 1353 | 3103 | 5025 | 8878
EHV Sub Cable | C2 | 1684 | 1933 | 4432 | 7178 | 12683
EHV Sub Cable | C3 | 2525 | 2900 | 6649 | 10767 | 19024
EHV Sub Cable | C4 | 4209 | 4833 | 11081 | 17946 | 31707
33kV CB (Air Insulated Busbars)(ID)(GM) | C1 | 318 | 365 | 837 | 1356 | 2396
33kV CB (Air Insulated Busbars)(ID)(GM) | C2 | 454 | 522 | 1196 | 1937 | 3423
33kV CB (Air Insulated Busbars)(ID)(GM) | C3 | 682 | 782 | 1794 | 2906 | 5134
33kV CB (Air Insulated Busbars)(ID)(GM) | C4 | 1136 | 1304 | 2990 | 4843 | 8557
33kV CB (Air Insulated Busbars)(OD)(GM) | C1 | 269 | 309 | 708 | 1147 | 2026
33kV CB (Air Insulated Busbars)(OD)(GM) | C2 | 384 | 441 | 1012 | 1638 | 2895
33kV CB (Air Insulated Busbars)(OD)(GM) | C3 | 576 | 662 | 1518 | 2458 | 4342
33kV CB (Air Insulated Busbars)(OD)(GM) | C4 | 961 | 1103 | 2529 | 4096 | 7237
33kV CB (Gas Insulated Busbars)(ID)(GM) | C1 | 351 | 403 | 925 | 1498 | 2646
33kV CB (Gas Insulated Busbars)(ID)(GM) | C2 | 502 | 576 | 1321 | 2140 | 3780
33kV CB (Gas Insulated Busbars)(ID)(GM) | C3 | 753 | 864 | 1982 | 3209 | 5670
33kV CB (Gas Insulated Busbars)(ID)(GM) | C4 | 1255 | 1440 | 3303 | 5349 | 9451
33kV CB (Gas Insulated Busbars)(OD)(GM) | C1 | 287 | 330 | 756 | 1225 | 2164
33kV CB (Gas Insulated Busbars)(OD)(GM) | C2 | 410 | 471 | 1080 | 1750 | 3092
33kV CB (Gas Insulated Busbars)(OD)(GM) | C3 | 616 | 707 | 1621 | 2625 | 4638
33kV CB (Gas Insulated Busbars)(OD)(GM) | C4 | 1026 | 1178 | 2701 | 4375 | 7730
33kV Switch (GM) | C1 | 235 | 270 | 619 | 1002 | 1771
33kV Switch (GM) | C2 | 336 | 386 | 884 | 1432 | 2530
33kV Switch (GM) | C3 | 504 | 579 | 1326 | 2148 | 3796
33kV Switch (GM) | C4 | 840 | 964 | 2211 | 3580 | 6326
33kV RMU | C1 | 302 | 347 | 796 | 1289 | 2277
33kV RMU | C2 | 432 | 496 | 1137 | 1841 | 3253
33kV RMU | C3 | 648 | 744 | 1705 | 2762 | 4879
33kV RMU | C4 | 1080 | 1239 | 2842 | 4603 | 8132
66kV CB (Air Insulated Busbars)(ID)(GM) | C1 | 877 | 1008 | 2310 | 3741 | 6610
66kV CB (Air Insulated Busbars)(ID)(GM) | C2 | 1254 | 1439 | 3300 | 5344 | 9443
66kV CB (Air Insulated Busbars)(ID)(GM) | C3 | 1880 | 2159 | 4950 | 8017 | 14164
66kV CB (Air Insulated Busbars)(ID)(GM) | C4 | 3134 | 3598 | 8250 | 13361 | 23607
66kV CB (Air Insulated Busbars)(OD)(GM) | C1 | 908 | 1042 | 2389 | 3869 | 6836
66kV CB (Air Insulated Busbars)(OD)(GM) | C2 | 1296 | 1489 | 3413 | 5527 | 9766
66kV CB (Air Insulated Busbars)(OD)(GM) | C3 | 1945 | 2233 | 5120 | 8291 | 14649
66kV CB (Air Insulated Busbars)(OD)(GM) | C4 | 3241 | 3721 | 8533 | 13819 | 24416
66kV CB (Gas Insulated Busbars)(ID)(GM) | C1 | 1115 | 1280 | 2935 | 4753 | 8399
66kV CB (Gas Insulated Busbars)(ID)(GM) | C2 | 1593 | 1829 | 4193 | 6791 | 11998
66kV CB (Gas Insulated Busbars)(ID)(GM) | C3 | 2389 | 2743 | 6290 | 10186 | 17997
66kV CB (Gas Insulated Busbars)(ID)(GM) | C4 | 3982 | 4572 | 10483 | 16977 | 29995
66kV CB (Gas Insulated Busbars)(OD)(GM) | C1 | 968 | 1111 | 2548 | 4127 | 7292
66kV CB (Gas Insulated Busbars)(OD)(GM) | C2 | 1383 | 1588 | 3641 | 5896 | 10417
66kV CB (Gas Insulated Busbars)(OD)(GM) | C3 | 2074 | 2382 | 5461 | 8844 | 15626
66kV CB (Gas Insulated Busbars)(OD)(GM) | C4 | 3457 | 3970 | 9102 | 14740 | 26044
33kV Transformer (GM) | C1 | 1424 | 1635 | 3748 | 6070 | 10725
33kV Transformer (GM) | C2 | 2034 | 2335 | 5354 | 8671 | 15321
33kV Transformer (GM) | C3 | 3051 | 3503 | 8031 | 13007 | 22981
33kV Transformer (GM) | C4 | 5085 | 5838 | 13385 | 21678 | 38302
Transformador 34kV (GM) | C1 | 1424 | 1635 | 3748 | 6070 | 10725
Transformador 34kV (GM) | C2 | 2034 | 2335 | 5354 | 8671 | 15321
Transformador 34kV (GM) | C3 | 3051 | 3503 | 8031 | 13007 | 22981
Transformador 34kV (GM) | C4 | 5085 | 5838 | 13385 | 21678 | 38302
66kV Transformer (GM) | C1 | 1850 | 2124 | 4871 | 7889 | 13938
66kV Transformer (GM) | C2 | 2643 | 3035 | 6958 | 11269 | 19911
66kV Transformer (GM) | C3 | 3965 | 4552 | 10438 | 16904 | 29867
66kV Transformer (GM) | C4 | 6608 | 7587 | 17396 | 28173 | 49778
132kV OHL (Tower Line) Conductor | C1 | 46 | 53 | 120 | 195 | 345
132kV OHL (Tower Line) Conductor | C2 | 65 | 75 | 172 | 279 | 493
132kV OHL (Tower Line) Conductor | C3 | 98 | 113 | 258 | 418 | 739
132kV OHL (Tower Line) Conductor | C4 | 163 | 188 | 430 | 697 | 1231
132kV Tower | C1 | 210 | 241 | 554 | 897 | 1584
132kV Tower | C2 | 300 | 345 | 791 | 1281 | 2263
132kV Tower | C3 | 451 | 517 | 1186 | 1921 | 3395
132kV Tower | C4 | 751 | 862 | 1977 | 3202 | 5658
132kV Fittings | C1 | 7 | 8 | 17 | 28 | 49
132kV Fittings | C2 | 9 | 11 | 25 | 40 | 71
132kV Fittings | C3 | 14 | 16 | 37 | 60 | 106
132kV Fittings | C4 | 23 | 27 | 62 | 100 | 176
132kV UG Cable (Non Pressurised) | C1 | 1680 | 1929 | 4423 | 7163 | 12655
132kV UG Cable (Non Pressurised) | C2 | 2400 | 2756 | 6318 | 10232 | 18079
132kV UG Cable (Non Pressurised) | C3 | 3600 | 4133 | 9477 | 15348 | 27118
132kV UG Cable (Non Pressurised) | C4 | 6000 | 6889 | 15795 | 25581 | 45197
132kV UG Cable (Oil) | C1 | 3169 | 3638 | 8341 | 13509 | 23868
132kV UG Cable (Oil) | C2 | 4527 | 5197 | 11916 | 19298 | 34098
132kV UG Cable (Oil) | C3 | 6790 | 7796 | 17874 | 28948 | 51147
132kV UG Cable (Oil) | C4 | 11316 | 12993 | 29791 | 48246 | 85244
132kV UG Cable (Gas) | C1 | 953 | 1094 | 2508 | 4062 | 7176
132kV UG Cable (Gas) | C2 | 1361 | 1563 | 3583 | 5802 | 10252
132kV UG Cable (Gas) | C3 | 2041 | 2344 | 5374 | 8703 | 15378
132kV UG Cable (Gas) | C4 | 3402 | 3907 | 8957 | 14506 | 25629
132kV Sub Cable | C1 | 2022 | 2322 | 5324 | 8622 | 15233
132kV Sub Cable | C2 | 2889 | 3317 | 7605 | 12316 | 21761
132kV Sub Cable | C3 | 4333 | 4975 | 11408 | 18475 | 32642
132kV Sub Cable | C4 | 7222 | 8292 | 19013 | 30791 | 54403
132kV CB (Air Insulated Busbars)(ID)(GM) | C1 | 2518 | 2892 | 6630 | 10737 | 18971
132kV CB (Air Insulated Busbars)(ID)(GM) | C2 | 3598 | 4131 | 9471 | 15338 | 27101
132kV CB (Air Insulated Busbars)(ID)(GM) | C3 | 5397 | 6196 | 14207 | 23008 | 40651
132kV CB (Air Insulated Busbars)(ID)(GM) | C4 | 8995 | 10327 | 23678 | 38346 | 67752
132kV CB (Air Insulated Busbars)(OD)(GM) | C1 | 1160 | 1332 | 3054 | 4947 | 8740
132kV CB (Air Insulated Busbars)(OD)(GM) | C2 | 1658 | 1903 | 4363 | 7066 | 12485
132kV CB (Air Insulated Busbars)(OD)(GM) | C3 | 2486 | 2855 | 6545 | 10600 | 18728
132kV CB (Air Insulated Busbars)(OD)(GM) | C4 | 4144 | 4758 | 10908 | 17666 | 31214
132kV CB (Gas Insulated Busbars)(ID)(GM) | C1 | 3273 | 3758 | 8617 | 13956 | 24657
132kV CB (Gas Insulated Busbars)(ID)(GM) | C2 | 4676 | 5369 | 12310 | 19937 | 35225
132kV CB (Gas Insulated Busbars)(ID)(GM) | C3 | 7015 | 8054 | 18465 | 29905 | 52837
132kV CB (Gas Insulated Busbars)(ID)(GM) | C4 | 11691 | 13423 | 30776 | 49841 | 88062
132kV CB (Gas Insulated Busbars)(OD)(GM) | C1 | 2284 | 2623 | 6013 | 9738 | 17206
132kV CB (Gas Insulated Busbars)(OD)(GM) | C2 | 3263 | 3747 | 8590 | 13912 | 24580
132kV CB (Gas Insulated Busbars)(OD)(GM) | C3 | 4895 | 5620 | 12885 | 20868 | 36870
132kV CB (Gas Insulated Busbars)(OD)(GM) | C4 | 8158 | 9367 | 21475 | 34780 | 61450
132kV Transformer (GM) | C1 | 5115 | 5873 | 13465 | 21807 | 38530
132kV Transformer (GM) | C2 | 7307 | 8390 | 19236 | 31153 | 55042
132kV Transformer (GM) | C3 | 10960 | 12584 | 28853 | 46729 | 82563
132kV Transformer (GM) | C4 | 18267 | 20974 | 48089 | 77882 | 137606

## 239
Asset Register Category | Forecast Ageing Rate | Comments
LV Poles | 0.043598 | From Normal Expected Life for Wood Pole subdivision
LV Circuit Breaker | 0.039965
LV Pillar (ID) | 0.039965
LV Pillar (OD at Substation) | 0.039965
LV Pillar (OD not at a Substation) | 0.039965
LV Board (WM) | 0.039965
LV UGB | 0.043598
LV Board (X-type Network) (WM) | 0.039965
6.6/11kV Poles | 0.043598 | From Normal Expected Life for Wood Pole subdivision
20kV Poles | 0.043598 | From Normal Expected Life for Wood Pole subdivision
HV Sub Cable | 0.039965
6.6/11kV CB (GM) Primary | 0.043598
6.6/11kV CB (GM) Secondary | 0.043598
6.6/11kV Switch (GM) | 0.043598
6.6/11kV RMU | 0.043598
6.6/11kV X-type RMU | 0.043598
20kV CB (GM) Primary | 0.043598
20kV CB (GM) Secondary | 0.043598
20kV Switch (GM) | 0.043598
20kV RMU | 0.043598
6.6/11kV Transformer (GM) | 0.039965
20kV Transformer (GM) | 0.039965
33kV Pole | 0.043598 | From Normal Expected Life for Wood Pole subdivision
66kV Pole | 0.043598 | From Normal Expected Life for Wood Pole subdivision
33kV OHL (Tower Line) Conductor | 0.043598 | From Normal Expected Life for ACSR - greased subdivision
33kV Tower | 0.029974 | From Normal Expected Life for Steelwork subcomponent
33kV Fittings | 0.059947
66kV OHL (Tower Line) Conductor | 0.043598 | From Normal Expected Life for ACSR - greased subdivision
66kV Tower | 0.029974 | From Normal Expected Life for Steelwork subcomponent
66kV Fittings | 0.059947
33kV UG Cable (Non Pressurised) | 0.023979
33kV UG Cable (Oil) | 0.031972 | From Normal Expected Life for Aluminium Sheath - Copper Conductor subdivision
33kV UG Cable (Gas) | 0.034256 | From Normal Expected Life for Aluminium Sheath - Copper Conductor subdivision
66kV UG Cable (Non Pressurised) | 0.023979
66kV UG Cable (Oil) | 0.031972 | From Normal Expected Life for Aluminium Sheath - Copper Conductor subdivision
66kV UG Cable (Gas) | 0.034256 | From Normal Expected Life for Aluminium Sheath - Copper Conductor subdivision
EHV Sub Cable | 0.039965
33kV CB (Air Insulated Busbars)(ID)(GM) | 0.039965
33kV CB (Air Insulated Busbars)(OD) (GM) | 0.047958
33kV CB (Gas Insulated Busbars)(ID)(GM) | 0.039965
33kV CB (Gas Insulated Busbars)(OD)(GM) | 0.047958
33kV Switch (GM) | 0.043598
33kV RMU | 0.043598
66kV CB (Air Insulated Busbars)(ID)(GM) | 0.047958
66kV CB (Air Insulated Busbars)(OD)(GM) | 0.043598
66kV CB (Gas Insulated Busbars)(ID)(GM) | 0.043598
66kV CB (Gas Insulated Busbars)(OD)(GM) | 0.047958
33kV Transformer (GM) | 0.039965 | From Normal Expected Life for Transformer - Pre 1980 subcomponent and subdivision
Transformador 34kV (GM) | 0.039965 | From Normal Expected Life for Transformer - Pre 1980 subcomponent and subdivision
66kV Transformer (GM) | 0.039965 | From Normal Expected Life for Transformer - Pre 1980 subcomponent and subdivision
132kV OHL (Tower Line) Conductor | 0.043598 | From Normal Expected Life for ACSR - greased subdivision
132kV Tower | 0.029974 | From Normal Expected Life for Steelwork subcomponent
132kV Fittings | 0.059947
132kV UG Cable (Non Pressurised) | 0.023979
132kV UG Cable (Oil) | 0.031972 | From Normal Expected Life for Aluminium Sheath - Copper Conductor subdivision
132kV UG Cable (Gas) | 0.034256 | From Normal Expected Life for Aluminium Sheath - Copper Conductor subdivision
132kV Sub Cable | 0.039965
132kV CB (Air Insulated Busbars)(ID)(GM) | 0.039965
132kV CB (Air Insulated Busbars)(OD)(GM) | 0.047958
132kV CB (Gas Insulated Busbars)(ID)(GM) | 0.039965
132kV CB (Gas Insulated Busbars)(OD)(GM) | 0.043598
132kV Transformer (GM) | 0.039965 | From Normal Expected Life for Transformer - Pre 1980 subcomponent and subdivision

## 240
Asset Register Category | HI1: Typical Cumulative Discounted POF Weightings for Each Health Index Band | HI2: Typical Cumulative Discounted POF Weightings for Each Health Index Band | HI3: Typical Cumulative Discounted POF Weightings for Each Health Index Band | HI4: Typical Cumulative Discounted POF Weightings for Each Health Index Band | HI5: Typical Cumulative Discounted POF Weightings for Each Health Index Band
LV Poles | 0.1595 | 0.6526 | 1.3389 | 2.1126 | 3.0838
LV Circuit Breaker | 0.0227 | 0.082 | 0.1708 | 0.2801 | 0.4269
LV Pillar (ID) | 0.0254 | 0.0919 | 0.1916 | 0.3143 | 0.479
LV Pillar (OD at Substation) | 0.0254 | 0.0919 | 0.1916 | 0.3143 | 0.479
LV Pillar (OD not at a Substation) | 0.0254 | 0.0919 | 0.1916 | 0.3143 | 0.479
LV Board (WM) | 0.0382 | 0.1379 | 0.2875 | 0.4715 | 0.7184
LV UGB | 0.0431 | 0.1763 | 0.3617 | 0.5708 | 0.8332
LV Board (X-type Network) (WM) | 0.0382 | 0.1379 | 0.2875 | 0.4715 | 0.7184
6.6/11kV Poles | 0.1595 | 0.6526 | 1.3389 | 2.1126 | 3.0838
20kV Poles | 0.1595 | 0.6526 | 1.3389 | 2.1126 | 3.0838
HV Sub Cable | 0.1117 | 0.4038 | 0.8416 | 1.3802 | 2.1032
6.6/11kV CB (GM) Primary | 0.0291 | 0.1191 | 0.2443 | 0.3855 | 0.5627
6.6/11kV CB (GM) Secondary | 0.0375 | 0.1534 | 0.3148 | 0.4966 | 0.725
6.6/11kV Switch (GM) | 0.0375 | 0.1534 | 0.3148 | 0.4966 | 0.725
6.6/11kV RMU | 0.0375 | 0.1534 | 0.3148 | 0.4966 | 0.725
6.6/11kV X-type RMU | 0.0375 | 0.1534 | 0.3148 | 0.4966 | 0.725
20kV CB (GM) Primary | 0.0291 | 0.1191 | 0.2443 | 0.3855 | 0.5627
20kV CB (GM) Secondary | 0.0375 | 0.1534 | 0.3148 | 0.4966 | 0.725
20kV Switch (GM) | 0.0375 | 0.1534 | 0.3148 | 0.4966 | 0.725
20kV RMU | 0.0375 | 0.1534 | 0.3148 | 0.4966 | 0.725
6.6/11kV Transformer (GM) | 0.0431 | 0.1559 | 0.325 | 0.533 | 0.8121
20kV Transformer (GM) | 0.0431 | 0.1559 | 0.325 | 0.533 | 0.8121
33kV Pole | 0.1595 | 0.6526 | 1.3389 | 2.1126 | 3.0838
66kV Pole | 0.1595 | 0.6526 | 1.3389 | 2.1126 | 3.0838
33kV OHL (Tower Line) Conductor | 0.0448 | 0.1832 | 0.3758 | 0.593 | 0.8656
33kV Tower | 0.3012 | 0.7709 | 1.6673 | 2.7647 | 4.8615
33kV Fittings | 0.0694 | 0.4162 | 0.6737 | 0.8979 | 1.1667
66kV OHL (Tower Line) Conductor | 0.0448 | 0.1832 | 0.3758 | 0.593 | 0.8656
66kV Tower | 0.3012 | 0.7709 | 1.6673 | 2.7647 | 4.8615
66kV Fittings | 0.0694 | 0.4162 | 0.6737 | 0.8979 | 1.1667
33kV UG Cable (Non Pressurised) | 0.3637 | 0.7714 | 1.6978 | 2.8015 | 5.0373
33kV UG Cable (Oil) | 11.5754 | 31.6439 | 67.9831 | 112.9162 | 194.2315
33kV UG Cable (Gas) | 24.8906 | 73.5116 | 156.6694 | 260.7076 | 433.9966
66kV UG Cable (Non Pressurised) | 0.3637 | 0.7714 | 1.6978 | 2.8015 | 5.0373
66kV UG Cable (Oil) | 11.5754 | 31.6439 | 67.9831 | 112.9162 | 194.2315
66kV UG Cable (Gas) | 24.8906 | 73.5116 | 156.6694 | 260.7076 | 433.9966
EHV Sub Cable | 0.1117 | 0.4038 | 0.8416 | 1.3802 | 2.1032
33kV CB (Air Insulated Busbars)(ID)(GM) | 0.1234 | 0.4457 | 0.9291 | 1.5237 | 2.3219
33kV CB (Air Insulated Busbars)(OD)(GM) | 0.1291 | 0.6052 | 1.2054 | 1.7886 | 2.5091
33kV CB (Gas Insulated Busbars)(ID)(GM) | 0.1234 | 0.4457 | 0.9291 | 1.5237 | 2.3219
33kV CB (Gas Insulated Busbars)(OD)(GM) | 0.1291 | 0.6052 | 1.2054 | 1.7886 | 2.5091
33kV Switch (GM) | 0.1248 | 0.5106 | 1.0476 | 1.653 | 2.4129
33kV RMU | 0.1248 | 0.5106 | 1.0476 | 1.653 | 2.4129
66kV CB (Air Insulated Busbars)(ID)(GM) | 0.2963 | 1.3896 | 2.7676 | 4.1066 | 5.7609
66kV CB (Air Insulated Busbars)(OD)(GM) | 0.2865 | 1.1723 | 2.4053 | 3.7953 | 5.54
66kV CB (Gas Insulated Busbars)(ID)(GM) | 0.2865 | 1.1723 | 2.4053 | 3.7953 | 5.54
66kV CB (Gas Insulated Busbars)(OD)(GM) | 0.2963 | 1.3896 | 2.7676 | 4.1066 | 5.7609
33kV Transformer (GM) | 0.2511 | 0.9075 | 1.8915 | 3.1021 | 4.7271
Transformador 34kV (GM) | 0.2511 | 0.9075 | 1.8915 | 3.1021 | 4.7271
66kV Transformer (GM) | 0.2511 | 0.9075 | 1.8915 | 3.1021 | 4.7271
132kV OHL (Tower Line) Conductor | 0.0448 | 0.1832 | 0.3758 | 0.593 | 0.8656
132kV Tower | 0.3012 | 0.7709 | 1.6673 | 2.7647 | 4.8615
132kV Fittings | 0.0694 | 0.4162 | 0.6737 | 0.8979 | 1.1667
132kV UG Cable (Non Pressurised) | 0.3637 | 0.7714 | 1.6978 | 2.8015 | 5.0373
132kV UG Cable (Oil) | 11.5754 | 31.6439 | 67.9831 | 112.9162 | 194.2315
132kV UG Cable (Gas) | 24.8906 | 73.5116 | 156.6694 | 260.7076 | 433.9966
132kV Sub Cable | 0.1117 | 0.4038 | 0.8416 | 1.3802 | 2.1032
132kV CB (Air Insulated Busbars)(ID)(GM) | 0.2384 | 0.8615 | 1.7957 | 2.945 | 4.4876
132kV CB (Air Insulated Busbars)(OD)(GM) | 0.2495 | 1.1697 | 2.3297 | 3.4569 | 4.8495
132kV CB (Gas Insulated Busbars)(ID)(GM) | 0.2384 | 0.8615 | 1.7957 | 2.945 | 4.4876
132kV CB (Gas Insulated Busbars)(OD)(GM) | 0.2412 | 0.9869 | 2.0248 | 3.1948 | 4.6636
132kV Transformer (GM) | 0.2511 | 0.9075 | 1.8915 | 3.1021 | 4.7271

## 241
Asset Register Category | Criticality Index Band | HI1: Risk Index or Monetised Long Term Risk Weighting (£ at 20/21 prices) For Each Health Index Band | HI2: Risk Index or Monetised Long Term Risk Weighting (£ at 20/21 prices) For Each Health Index Band | HI3: Risk Index or Monetised Long Term Risk Weighting (£ at 20/21 prices) For Each Health Index Band | HI4: Risk Index or Monetised Long Term Risk Weighting (£ at 20/21 prices) For Each Health Index Band | HI5: Risk Index or Monetised Long Term Risk Weighting (£ at 20/21 prices) For Each Health Index Band
LV Poles | C1 | 287 | 1174 | 2408 | 3800 | 5547
LV Poles | C2 | 410 | 1677 | 3441 | 5429 | 7924
LV Poles | C3 | 615 | 2515 | 5161 | 8143 | 11887
LV Poles | C4 | 1025 | 4192 | 8601 | 13572 | 19811
LV Circuit Breaker | C1 | 386 | 1394 | 2904 | 4762 | 7257
LV Circuit Breaker | C2 | 551 | 1991 | 4148 | 6802 | 10367
LV Circuit Breaker | C3 | 827 | 2987 | 6222 | 10203 | 15551
LV Circuit Breaker | C4 | 1378 | 4978 | 10370 | 17006 | 25918
LV Pillar (ID) | C1 | 410 | 1482 | 3090 | 5069 | 7726
LV Pillar (ID) | C2 | 585 | 2118 | 4415 | 7242 | 11037
LV Pillar (ID) | C3 | 878 | 3176 | 6622 | 10863 | 16556
LV Pillar (ID) | C4 | 1463 | 5294 | 11037 | 18105 | 27593
LV Pillar (OD at Substation) | C1 | 419 | 1515 | 3158 | 5180 | 7894
LV Pillar (OD at Substation) | C2 | 598 | 2164 | 4511 | 7400 | 11277
LV Pillar (OD at Substation) | C3 | 897 | 3245 | 6766 | 11100 | 16916
LV Pillar (OD at Substation) | C4 | 1495 | 5409 | 11277 | 18499 | 28193
LV Pillar (OD not at a Substation) | C1 | 379 | 1371 | 2859 | 4690 | 7147
LV Pillar (OD not at a Substation) | C2 | 541 | 1959 | 4084 | 6700 | 10210
LV Pillar (OD not at a Substation) | C3 | 812 | 2938 | 6126 | 10049 | 15315
LV Pillar (OD not at a Substation) | C4 | 1354 | 4897 | 10210 | 16749 | 25526
LV Board (WM) | C1 | 674 | 2433 | 5073 | 8319 | 12676
LV Board (WM) | C2 | 963 | 3476 | 7247 | 11885 | 18108
LV Board (WM) | C3 | 1444 | 5214 | 10870 | 17827 | 27162
LV Board (WM) | C4 | 2407 | 8690 | 18117 | 29712 | 45271
LV UGB | C1 | 479 | 1960 | 4022 | 6346 | 9264
LV UGB | C2 | 685 | 2800 | 5745 | 9066 | 13234
LV UGB | C3 | 1027 | 4200 | 8618 | 13599 | 19851
LV UGB | C4 | 1711 | 7001 | 14363 | 22666 | 33085
LV Board (X-type Network) (WM) | C1 | 712 | 2569 | 5357 | 8785 | 13385
LV Board (X-type Network) (WM) | C2 | 1017 | 3671 | 7652 | 12550 | 19122
LV Board (X-type Network) (WM) | C3 | 1525 | 5506 | 11479 | 18825 | 28683
LV Board (X-type Network) (WM) | C4 | 2542 | 9176 | 19131 | 31375 | 47804
6.6/11kV Poles | C1 | 461 | 1888 | 3874 | 6112 | 8922
6.6/11kV Poles | C2 | 659 | 2697 | 5534 | 8732 | 12746
6.6/11kV Poles | C3 | 989 | 4046 | 8301 | 13098 | 19119
6.6/11kV Poles | C4 | 1648 | 6743 | 13835 | 21830 | 31865
20kV Poles | C1 | 504 | 2063 | 4232 | 6678 | 9747
20kV Poles | C2 | 720 | 2947 | 6046 | 9539 | 13925
20kV Poles | C3 | 1080 | 4420 | 9069 | 14309 | 20887
20kV Poles | C4 | 1801 | 7367 | 15114 | 23848 | 34812
HV Sub Cable | C1 | 29395 | 106264 | 221475 | 363212 | 553476
HV Sub Cable | C2 | 41993 | 151805 | 316393 | 518875 | 790681
HV Sub Cable | C3 | 62989 | 227708 | 474589 | 778312 | 1186021
HV Sub Cable | C4 | 104982 | 379513 | 790981 | 1297187 | 1976702
6.6/11kV CB (GM) Primary | C1 | 1490 | 6100 | 12512 | 19743 | 28819
6.6/11kV CB (GM) Primary | C2 | 2129 | 8714 | 17874 | 28205 | 41170
6.6/11kV CB (GM) Primary | C3 | 3194 | 13071 | 26811 | 42307 | 61755
6.6/11kV CB (GM) Primary | C4 | 5323 | 21785 | 44685 | 70512 | 102924
6.6/11kV CB (GM) Secondary | C1 | 652 | 2668 | 5475 | 8638 | 12610
6.6/11kV CB (GM) Secondary | C2 | 932 | 3812 | 7822 | 12339 | 18015
6.6/11kV CB (GM) Secondary | C3 | 1398 | 5717 | 11733 | 18509 | 27022
6.6/11kV CB (GM) Secondary | C4 | 2329 | 9529 | 19555 | 30849 | 45037
6.6/11kV Switch (GM) | C1 | 608 | 2486 | 5103 | 8049 | 11752
6.6/11kV Switch (GM) | C2 | 868 | 3552 | 7289 | 11499 | 16788
6.6/11kV Switch (GM) | C3 | 1303 | 5328 | 10934 | 17249 | 25182
6.6/11kV Switch (GM) | C4 | 2171 | 8880 | 18224 | 28748 | 41970
6.6/11kV RMU | C1 | 728 | 2977 | 6110 | 9639 | 14072
6.6/11kV RMU | C2 | 1040 | 4253 | 8729 | 13770 | 20103
6.6/11kV RMU | C3 | 1560 | 6380 | 13093 | 20655 | 30154
6.6/11kV RMU | C4 | 2599 | 10634 | 21822 | 34424 | 50257
6.6/11kV X-type RMU | C1 | 819 | 3351 | 6876 | 10847 | 15836
6.6/11kV X-type RMU | C2 | 1170 | 4787 | 9823 | 15496 | 22622
6.6/11kV X-type RMU | C3 | 1755 | 7180 | 14734 | 23243 | 33934
6.6/11kV X-type RMU | C4 | 2925 | 11966 | 24557 | 38739 | 56556
20kV CB (GM) Primary | C1 | 1529 | 6260 | 12840 | 20261 | 29574
20kV CB (GM) Primary | C2 | 2185 | 8942 | 18343 | 28944 | 42249
20kV CB (GM) Primary | C3 | 3277 | 13413 | 27514 | 43416 | 63373
20kV CB (GM) Primary | C4 | 5462 | 22356 | 45857 | 72361 | 105622
20kV CB (GM) Secondary | C1 | 659 | 2696 | 5532 | 8726 | 12740
20kV CB (GM) Secondary | C2 | 941 | 3851 | 7902 | 12466 | 18199
20kV CB (GM) Secondary | C3 | 1412 | 5776 | 11854 | 18699 | 27299
20kV CB (GM) Secondary | C4 | 2353 | 9627 | 19756 | 31165 | 45499
20kV Switch (GM) | C1 | 630 | 2576 | 5287 | 8341 | 12177
20kV Switch (GM) | C2 | 900 | 3681 | 7553 | 11915 | 17395
20kV Switch (GM) | C3 | 1350 | 5521 | 11330 | 17873 | 26093
20kV Switch (GM) | C4 | 2249 | 9201 | 18883 | 29788 | 43488
20kV RMU | C1 | 733 | 2997 | 6151 | 9703 | 14166
20kV RMU | C2 | 1047 | 4282 | 8787 | 13861 | 20237
20kV RMU | C3 | 1570 | 6423 | 13180 | 20792 | 30355
20kV RMU | C4 | 2617 | 10704 | 21967 | 34653 | 50591
6.6/11kV Transformer (GM) | C1 | 672 | 2430 | 5067 | 8309 | 12661
6.6/11kV Transformer (GM) | C2 | 960 | 3472 | 7238 | 11871 | 18087
6.6/11kV Transformer (GM) | C3 | 1440 | 5208 | 10857 | 17806 | 27130
6.6/11kV Transformer (GM) | C4 | 2400 | 8680 | 18095 | 29677 | 45216
20kV Transformer (GM) | C1 | 711 | 2571 | 5360 | 8790 | 13393
20kV Transformer (GM) | C2 | 1015 | 3673 | 7657 | 12557 | 19133
20kV Transformer (GM) | C3 | 1523 | 5509 | 11485 | 18836 | 28699
20kV Transformer (GM) | C4 | 2539 | 9182 | 19142 | 31394 | 47832
33kV Pole | C1 | 318 | 1301 | 2669 | 4211 | 6146
33kV Pole | C2 | 454 | 1858 | 3812 | 6015 | 8781
33kV Pole | C3 | 681 | 2787 | 5718 | 9023 | 13171
33kV Pole | C4 | 1135 | 4645 | 9531 | 15038 | 21952
66kV Pole | C1 | 468 | 1915 | 3928 | 6198 | 9047
66kV Pole | C2 | 668 | 2735 | 5611 | 8854 | 12924
66kV Pole | C3 | 1003 | 4103 | 8417 | 13281 | 19387
66kV Pole | C4 | 1671 | 6838 | 14029 | 22135 | 32311
33kV OHL (Tower Line) Conductor | C1 | 650 | 2659 | 5453 | 8605 | 12561
33kV OHL (Tower Line) Conductor | C2 | 929 | 3798 | 7791 | 12293 | 17945
33kV OHL (Tower Line) Conductor | C3 | 1393 | 5697 | 11686 | 18440 | 26917
33kV OHL (Tower Line) Conductor | C4 | 2322 | 9495 | 19477 | 30733 | 44861
33kV Tower | C1 | 1664 | 4259 | 9212 | 15275 | 26860
33kV Tower | C2 | 2377 | 6085 | 13160 | 21822 | 38372
33kV Tower | C3 | 3566 | 9127 | 19740 | 32732 | 57557
33kV Tower | C4 | 5943 | 15212 | 32900 | 54554 | 95929
33kV Fittings | C1 | 102 | 611 | 990 | 1319 | 1714
33kV Fittings | C2 | 146 | 873 | 1414 | 1884 | 2448
33kV Fittings | C3 | 218 | 1310 | 2121 | 2826 | 3672
33kV Fittings | C4 | 364 | 2183 | 3534 | 4710 | 6121
66kV OHL (Tower Line) Conductor | C1 | 874 | 3574 | 7332 | 11569 | 16888
66kV OHL (Tower Line) Conductor | C2 | 1249 | 5106 | 10474 | 16528 | 24125
66kV OHL (Tower Line) Conductor | C3 | 1873 | 7659 | 15711 | 24792 | 36188
66kV OHL (Tower Line) Conductor | C4 | 3122 | 12765 | 26185 | 41319 | 60314
66kV Tower | C1 | 3136 | 8026 | 17358 | 28783 | 50612
66kV Tower | C2 | 4480 | 11465 | 24797 | 41118 | 72303
66kV Tower | C3 | 6719 | 17198 | 37195 | 61677 | 108454
66kV Tower | C4 | 11199 | 28663 | 61992 | 102795 | 180757
66kV Fittings | C1 | 118 | 708 | 1146 | 1527 | 1984
66kV Fittings | C2 | 169 | 1011 | 1637 | 2181 | 2834
66kV Fittings | C3 | 253 | 1517 | 2455 | 3272 | 4252
66kV Fittings | C4 | 422 | 2528 | 4092 | 5454 | 7086
33kV UG Cable (Non Pressurised) | C1 | 9140 | 19386 | 42667 | 70404 | 126592
33kV UG Cable (Non Pressurised) | C2 | 13057 | 27694 | 60953 | 100578 | 180846
33kV UG Cable (Non Pressurised) | C3 | 19586 | 41542 | 91430 | 150867 | 271269
33kV UG Cable (Non Pressurised) | C4 | 32643 | 69236 | 152384 | 251444 | 452115
33kV UG Cable (Oil) | C1 | 48772 | 133329 | 286441 | 475762 | 818377
33kV UG Cable (Oil) | C2 | 69674 | 190469 | 409200 | 679660 | 1169109
33kV UG Cable (Oil) | C3 | 104511 | 285704 | 613801 | 1019490 | 1753664
33kV UG Cable (Oil) | C4 | 174185 | 476174 | 1023002 | 1699151 | 2922774
33kV UG Cable (Gas) | C1 | 7097 | 20960 | 44670 | 74333 | 123741
33kV UG Cable (Gas) | C2 | 10138 | 29942 | 63813 | 106189 | 176771
33kV UG Cable (Gas) | C3 | 15207 | 44913 | 95720 | 159285 | 265159
33kV UG Cable (Gas) | C4 | 25346 | 74855 | 159533 | 265473 | 441930
66kV UG Cable (Non Pressurised) | C1 | 18282 | 38775 | 85341 | 140819 | 253203
66kV UG Cable (Non Pressurised) | C2 | 26117 | 55393 | 121916 | 201170 | 361719
66kV UG Cable (Non Pressurised) | C3 | 39175 | 83089 | 182874 | 301755 | 542578
66kV UG Cable (Non Pressurised) | C4 | 65291 | 138482 | 304789 | 502926 | 904297
66kV UG Cable (Oil) | C1 | 48886 | 133640 | 287109 | 476872 | 820286
66kV UG Cable (Oil) | C2 | 69837 | 190914 | 410156 | 681247 | 1171839
66kV UG Cable (Oil) | C3 | 104755 | 286371 | 615234 | 1021870 | 1757758
66kV UG Cable (Oil) | C4 | 174592 | 477286 | 1025390 | 1703117 | 2929598
66kV UG Cable (Gas) | C1 | 11238 | 33189 | 70733 | 117704 | 195941
66kV UG Cable (Gas) | C2 | 16054 | 47413 | 101047 | 168149 | 279915
66kV UG Cable (Gas) | C3 | 24080 | 71119 | 151570 | 252222 | 419870
66kV UG Cable (Gas) | C4 | 40134 | 118532 | 252617 | 420370 | 699785
EHV Sub Cable | C1 | 22867 | 82665 | 172290 | 282551 | 430562
EHV Sub Cable | C2 | 32667 | 118093 | 246129 | 403644 | 615088
EHV Sub Cable | C3 | 49001 | 177139 | 369193 | 605466 | 922632
EHV Sub Cable | C4 | 81668 | 295232 | 615322 | 1009110 | 1537720
33kV CB (Air Insulated Busbars)(ID)(GM) | C1 | 6175 | 22304 | 46495 | 76251 | 116196
33kV CB (Air Insulated Busbars)(ID)(GM) | C2 | 8822 | 31863 | 66422 | 108930 | 165994
33kV CB (Air Insulated Busbars)(ID)(GM) | C3 | 13233 | 47795 | 99633 | 163395 | 248990
33kV CB (Air Insulated Busbars)(ID)(GM) | C4 | 22055 | 79658 | 166054 | 272325 | 414984
33kV CB (Air Insulated Busbars)(OD)(GM) | C1 | 5464 | 25616 | 51021 | 75706 | 106202
33kV CB (Air Insulated Busbars)(OD)(GM) | C2 | 7806 | 36594 | 72887 | 108151 | 151717
33kV CB (Air Insulated Busbars)(OD)(GM) | C3 | 11709 | 54892 | 109330 | 162226 | 227576
33kV CB (Air Insulated Busbars)(OD)(GM) | C4 | 19516 | 91486 | 182217 | 270377 | 379293
33kV CB (Gas Insulated Busbars)(ID)(GM) | C1 | 6821 | 24635 | 51354 | 84219 | 128337
33kV CB (Gas Insulated Busbars)(ID)(GM) | C2 | 9744 | 35193 | 73362 | 120313 | 183339
33kV CB (Gas Insulated Busbars)(ID)(GM) | C3 | 14616 | 52789 | 110044 | 180469 | 275009
33kV CB (Gas Insulated Busbars)(ID)(GM) | C4 | 24359 | 87982 | 183406 | 300781 | 458347
33kV CB (Gas Insulated Busbars)(OD)(GM) | C1 | 5836 | 27359 | 54492 | 80856 | 113428
33kV CB (Gas Insulated Busbars)(OD)(GM) | C2 | 8337 | 39084 | 77846 | 115509 | 162039
33kV CB (Gas Insulated Busbars)(OD)(GM) | C3 | 12506 | 58626 | 116768 | 173264 | 243059
33kV CB (Gas Insulated Busbars)(OD)(GM) | C4 | 20843 | 97711 | 194614 | 288773 | 405098
33kV Switch (GM) | C1 | 4617 | 18891 | 38759 | 61157 | 89272
33kV Switch (GM) | C2 | 6596 | 26987 | 55370 | 87368 | 127532
33kV Switch (GM) | C3 | 9894 | 40481 | 83055 | 131052 | 191297
33kV Switch (GM) | C4 | 16490 | 67468 | 138425 | 218420 | 318829
33kV RMU | C1 | 5936 | 24285 | 49825 | 78618 | 114760
33kV RMU | C2 | 8479 | 34692 | 71178 | 112312 | 163943
33kV RMU | C3 | 12719 | 52039 | 106768 | 168468 | 245914
33kV RMU | C4 | 21199 | 86731 | 177946 | 280780 | 409857
66kV CB (Air Insulated Busbars)(ID)(GM) | C1 | 17818 | 83564 | 166430 | 246950 | 346432
66kV CB (Air Insulated Busbars)(ID)(GM) | C2 | 25454 | 119377 | 237757 | 352786 | 494903
66kV CB (Air Insulated Busbars)(ID)(GM) | C3 | 38181 | 179065 | 356635 | 529180 | 742354
66kV CB (Air Insulated Busbars)(ID)(GM) | C4 | 63636 | 298441 | 594392 | 881966 | 1237256
66kV CB (Air Insulated Busbars)(OD)(GM) | C1 | 17819 | 72911 | 149596 | 236047 | 344558
66kV CB (Air Insulated Busbars)(OD)(GM) | C2 | 25455 | 104158 | 213709 | 337210 | 492225
66kV CB (Air Insulated Busbars)(OD)(GM) | C3 | 38183 | 156237 | 320564 | 505815 | 738338
66kV CB (Air Insulated Busbars)(OD)(GM) | C4 | 63638 | 260395 | 534273 | 843024 | 1230563
66kV CB (Gas Insulated Busbars)(ID)(GM) | C1 | 21891 | 89572 | 183782 | 289988 | 423296
66kV CB (Gas Insulated Busbars)(ID)(GM) | C2 | 31272 | 127960 | 262546 | 414269 | 604708
66kV CB (Gas Insulated Busbars)(ID)(GM) | C3 | 46909 | 191940 | 393819 | 621403 | 907062
66kV CB (Gas Insulated Busbars)(ID)(GM) | C4 | 78181 | 319900 | 656365 | 1035672 | 1511770
66kV CB (Gas Insulated Busbars)(OD)(GM) | C1 | 19657 | 92188 | 183606 | 272436 | 382184
66kV CB (Gas Insulated Busbars)(OD)(GM) | C2 | 28081 | 131697 | 262294 | 389195 | 545978
66kV CB (Gas Insulated Busbars)(OD)(GM) | C3 | 42122 | 197545 | 393441 | 583792 | 818967
66kV CB (Gas Insulated Busbars)(OD)(GM) | C4 | 70203 | 329241 | 655734 | 972987 | 1364944
33kV Transformer (GM) | C1 | 27629 | 99853 | 208124 | 341328 | 520129
33kV Transformer (GM) | C2 | 39470 | 142648 | 297320 | 487612 | 743041
33kV Transformer (GM) | C3 | 59205 | 213972 | 445980 | 731417 | 1114562
33kV Transformer (GM) | C4 | 98674 | 356619 | 743301 | 1219029 | 1857603
Transformador 34kV (GM) | C1 | 27629 | 99853 | 208124 | 341328 | 520129
Transformador 34kV (GM) | C2 | 39470 | 142648 | 297320 | 487612 | 743041
Transformador 34kV (GM) | C3 | 59205 | 213972 | 445980 | 731417 | 1114562
Transformador 34kV (GM) | C4 | 98674 | 356619 | 743301 | 1219029 | 1857603
66kV Transformer (GM) | C1 | 35907 | 129772 | 270484 | 443599 | 675974
66kV Transformer (GM) | C2 | 51296 | 185389 | 386405 | 633713 | 965677
66kV Transformer (GM) | C3 | 76944 | 278083 | 579608 | 950570 | 1448515
66kV Transformer (GM) | C4 | 128240 | 463472 | 966014 | 1584283 | 2414192
132kV OHL (Tower Line) Conductor | C1 | 899 | 3678 | 7544 | 11905 | 17378
132kV OHL (Tower Line) Conductor | C2 | 1285 | 5254 | 10778 | 17007 | 24825
132kV OHL (Tower Line) Conductor | C3 | 1927 | 7881 | 16167 | 25510 | 37238
132kV OHL (Tower Line) Conductor | C4 | 3212 | 13135 | 26944 | 42517 | 62063
132kV Tower | C1 | 4078 | 10438 | 22576 | 37435 | 65826
132kV Tower | C2 | 5826 | 14912 | 32251 | 53478 | 94038
132kV Tower | C3 | 8739 | 22368 | 48377 | 80218 | 141056
132kV Tower | C4 | 14566 | 37279 | 80628 | 133696 | 235094
132kV Fittings | C1 | 166 | 997 | 1614 | 2152 | 2796
132kV Fittings | C2 | 238 | 1425 | 2306 | 3074 | 3994
132kV Fittings | C3 | 356 | 2137 | 3459 | 4611 | 5991
132kV Fittings | C4 | 594 | 3562 | 5766 | 7684 | 9985
132kV UG Cable (Non Pressurised) | C1 | 32582 | 69107 | 152099 | 250975 | 451272
132kV UG Cable (Non Pressurised) | C2 | 46546 | 98724 | 217284 | 358536 | 644674
132kV UG Cable (Non Pressurised) | C3 | 69820 | 148086 | 325927 | 537804 | 967011
132kV UG Cable (Non Pressurised) | C4 | 116366 | 246809 | 543211 | 896340 | 1611684
132kV UG Cable (Oil) | C1 | 61446 | 167976 | 360876 | 599395 | 1031043
132kV UG Cable (Oil) | C2 | 87780 | 239966 | 515538 | 856280 | 1472920
132kV UG Cable (Oil) | C3 | 131670 | 359949 | 773306 | 1284420 | 2209379
132kV UG Cable (Oil) | C4 | 219450 | 599914 | 1288843 | 2140698 | 3682297
132kV UG Cable (Gas) | C1 | 18474 | 54562 | 116283 | 193502 | 322121
132kV UG Cable (Gas) | C2 | 26392 | 77945 | 166118 | 276431 | 460171
132kV UG Cable (Gas) | C3 | 39588 | 116918 | 249178 | 414648 | 690259
132kV UG Cable (Gas) | C4 | 65980 | 194863 | 415296 | 691078 | 1150430
132kV Sub Cable | C1 | 39235 | 141837 | 295616 | 484801 | 738758
132kV Sub Cable | C2 | 56050 | 202624 | 422308 | 692573 | 1055369
132kV Sub Cable | C3 | 84075 | 303935 | 633462 | 1038860 | 1583053
132kV Sub Cable | C4 | 140125 | 506559 | 1055770 | 1731433 | 2638422
132kV CB (Air Insulated Busbars)(ID)(GM) | C1 | 48877 | 176625 | 368154 | 603784 | 920048
132kV CB (Air Insulated Busbars)(ID)(GM) | C2 | 69824 | 252321 | 525935 | 862548 | 1314354
132kV CB (Air Insulated Busbars)(ID)(GM) | C3 | 104736 | 378482 | 788902 | 1293823 | 1971531
132kV CB (Air Insulated Busbars)(ID)(GM) | C4 | 174560 | 630803 | 1314837 | 2156371 | 3285885
132kV CB (Air Insulated Busbars)(OD) (GM) | C1 | 23566 | 110482 | 220049 | 326517 | 458053
132kV CB (Air Insulated Busbars)(OD) (GM) | C2 | 33666 | 157832 | 314355 | 466452 | 654361
132kV CB (Air Insulated Busbars)(OD) (GM) | C3 | 50499 | 236748 | 471533 | 699679 | 981542
132kV CB (Air Insulated Busbars)(OD) (GM) | C4 | 84165 | 394580 | 785888 | 1166131 | 1635903
132kV CB (Gas Insulated Busbars)(ID)(GM) | C1 | 63529 | 229573 | 478518 | 784784 | 1195856
132kV CB (Gas Insulated Busbars)(ID)(GM) | C2 | 90755 | 327961 | 683597 | 1121120 | 1708366
132kV CB (Gas Insulated Busbars)(ID)(GM) | C3 | 136133 | 491941 | 1025396 | 1681679 | 2562548
132kV CB (Gas Insulated Busbars)(ID)(GM) | C4 | 226889 | 819902 | 1708994 | 2802799 | 4270914
132kV CB (Gas Insulated Busbars)(OD) (GM) | C1 | 44852 | 183516 | 376515 | 594078 | 867204
132kV CB (Gas Insulated Busbars)(OD) (GM) | C2 | 64074 | 262165 | 537878 | 848683 | 1238863
132kV CB (Gas Insulated Busbars)(OD) (GM) | C3 | 96110 | 393248 | 806817 | 1273025 | 1858294
132kV CB (Gas Insulated Busbars)(OD) (GM) | C4 | 160184 | 655413 | 1344696 | 2121708 | 3097157
132kV Transformer (GM) | C1 | 99261 | 358739 | 747719 | 1226276 | 1868646
132kV Transformer (GM) | C2 | 141802 | 512485 | 1068171 | 1751822 | 2669495
132kV Transformer (GM) | C3 | 212702 | 768727 | 1602256 | 2627734 | 4004242
132kV Transformer (GM) | C4 | 354504 | 1281212 | 2670427 | 4379556 | 6673737